THE FLORIDA STATE UNIVERSITY

DESIGN GUIDELINES AND SPECIFICATIONS

August 2010

Facilities Design and Construction Department

TABLE OF CONTENTS

INTRODUCTION ...	... 6

REVISION HISTORY: ...	. 6

May 2006: ...	...6

DIVISION 1 - GENERAL PLANNING AND DESIGN DATA ...	. 8

GENERAL CONTRACT GUIDELINES ...	... 9

GENERAL DESIGN GUIDELINES ...	.. 10

General Information ...	... 10

Visual Clutter ...	.. 12

Acoustical Treatment ...	.. 12

Accessibility Guidelines ...	. 13

Guidelines for Toxic/Hazardous Materials ...	.. 14

DESIGN CRITERIA FOR SPECIFIC SPACES ...	... 15

Design of Parking Structures ...	.. 15

Restroom Design ...	... 15

Classroom Design ...	. 15

Custodial Closet Design ...	. 16

DIVISION 2 - SITEWORK ...	... 18

AESTHETIC COMPATIBILITY ...	. 18

GENERAL GUIDELINES ...	... 18

SAFETY PROVISIONS, SECURITY PROVISIONS AND TEMPORARY SERVICES DURING

CONSTRUCTION ...	... 18

PARKING ...	. 21

DEMOLITION ...	... 21

EARTHWORK ...	... 22

PEST CONTROL ...	.. 23

UTILITY WORK ...	.. 23

PAVING ...	. 24

EXTERIOR SIGNAGE ...	.. 36

STORMWATER DRAINAGE GUIDELINES ...	.. 36

DIVISION 3 - CONCRETE ...	.. 37

GENERAL REQUIREMENTS ...	.. 37

EXTERIOR EXPOSED CONCRETE OR PRE-CAST STONE ...	.. 37

DIVISION 4 - MASONRY ...	. 38

GENERAL REQUIREMENTS ...	.. 38

DIVISION 5 - METALS ...	.. 40

EXTERIOR FERROUS METALS...	... 40

EXTERIOR METAL STUDWALLS...	.. 40

DIVISION 6 - WOOD AND PLASTICS ...	... 41

GENERAL REQUIREMENTS ...	.. 41

RESTROOM COUNTERTOPS ...	. 41

DIVISION 7 - THERMAL AND MOISTURE PROTECTION ...	.. 42

2

GENERAL REQUIREMENTS ...	.. 42

ROOFING ...	. 43

EXTERIOR CLOSURE ASSEMBLIES ...	... 43

GENERAL ROOFING GUIDELINES ...	.. 43

DIVISION 8 - DOORS AND WINDOWS ...	. 45

GENERAL DOOR GUIDELINES...	... 45

GENERAL HARDWARE GUIDELINES ...	... 46

General ...	.. 46

Keying ...	. 47

GENERAL DOOR AND HARDWARE GUIDELINES FOR SPECIFIC SPACES ...	. 49

Restrooms ...	.. 49

Custodial Closets ...	.. 49

Classrooms ...	... 49

1.	Classroom doors shall have wired glass view panels set in steel framing or stops according to code. ... 49

HOUSING GUIDELINES FOR DOOR HARDWARE AND CYLINDER BITTING ...	. 49

WINDOW GUIDELINES ...	. 50

DIVISION 9 - MATERIALS AND FINISHES ...	.. 52

GENERAL MATERIAL AND FINISH GUIDELINES ...	... 52

GENERAL FINISH REQUIREMENTS FOR SPECIFIC SPACES ...	.. 52

Restroom Floors ...	. 52

Custodial Closet Floors ...	. 52

CARPET ...	. 52

General Carpeting Design Guidelines ...	... 52

Carpeting And Related Products ...	.. 53

Use of Carpet ...	.. 53

Carpet Cleaning ...	. 54

1.     As job progresses, surplus adhesive squeezed out between joints shall be removed. ..	. 54

2.     Any stains remaining shall be removed by approved methods. ..	.. 54

General Carpeting Installation Guidelines ...	.. 54

Glue-Down Installation Guidelines ...	. 55

Carpet Warranty ...	... 55

RESILIENT FLOOR TILE ...	.. 55

General Considerations for Resilient Tile...	. 55

General Resilient Tile Installation Guidelines ...	... 56

Resilient Tile And Related Products ...	. 56

Resilient Tile Cleaning ...	... 56

Resilient Tile Warranty ...	.. 56

STUCCO AND PLASTER ...	.. 57

QUARRY TILE ...	.. 57

CERAMIC TILE ...	... 57

ACOUSTICAL CEILING TILE ...	... 57

PAINTING ...	... 58

DIVISION 10 - SPECIALTIES ...	... 59

GENERAL ACCESSORY REQUIREMENTS FOR SPECIFIC SPACES ...	. 59

Toilets ...	.. 59

Custodial Closets ...	.. 59

Classrooms ...	... 60

MARKERBOARDS AND TACKBOARDS ...	.. 60

SIGNAGE ...	.. 60

3

CONSTRUCTION SIGN ...	60

BUILDING PLAQUE ...	61

FIRE PROTECTION SPECIALTIES ...	61

LOUVERS ...	61

WALL AND CORNER GUARDS ...	61

DIVISION 11 - EQUIPMENT ...	62

CENTRAL VACUUM SYSTEMS ...	62

TRASH HANDLING EQUIPMENT ...	62

LOADING DOCK EQUIPMENT ...	62

DIVISION 12 - FURNISHINGS ...	63

GENERAL GUIDELINES ...	63

WINDOW TREATMENT ...	63

FIXED SEATING SYSTEMS ...	63

LABORATORY CASEWORK ...	64

DIVISION 14 - ELEVATORS CHAIR LIFTS AND DUMBWAITERS ...	65

DIVISION 15 - MECHANICAL UTILITIES AND EQUIPMENT ...	86

PLUMBING...	88

WATER BASED FIRE EXTINGUISHING SYSTEMS (WHERE REQUIRED) ...	89

HEATING AND STEAM ...	90

CENTRAL UTILITY PLANT (CUP) CENTRAL CHILLED WATER SYSTEM/BUILDING ...	91

INTERFACES ...	91

AIR CONDITIONING ...	92

FUME HOODS ...	93

REFRIGERANT MANAGEMENT REQUIREMENTS ...	94

GENERAL REQUIREMENTS ...	94

NEW EQUIPMENT GUIDELINES ...	95

NEW EQUIPMENT ID TAGS ...	95

NEW EQUIPMENT LEAK TESTING ...	95

DEMOLITION PROCEDURE FOR EQUIPMENT REMOVED BY CONTRACTORS ...	95

BUILDING AUTOMATION AND CENTRAL MONITORING SYSTEMS ...	96

FIRE ALARM SYSTEMS ...	96

SECTION 16000 - ELECTRICAL ...	.. 100

2.2	WIRES AND CABLES ...	.. 102

2.6	PANELBOARDS ...	.. 103

2.8	MOTORS, DISCONNECT SWITCHES AND STARTERS ...	.. 105

2.9	POWER GENERATION ...	.. 106

2.10	SERVICE AND DISTRIBUTION ...	... 108

ELECTRIC SERVICE: ...	... 108

METERING ...	.. 109

4

GROUNDING ...	.. 109

MEDIUM VOLTAGE CABLE ...	. 112

DUCT BANK SYSTEMS ...	.. 112

MANHOLES ...	. 112

LIGHTNING PROTECTION SYSTEMS ...	. 113

LIGHTING SYSTEMS ...	... 113

OUTDOOR LIGHTING ...	.. 115

PARKING DECK LIGHTING...	. 116

APPENDIX A - FSU Telecommunications Infrastructure Standard (r2.2G, 05/22/2006) APPENDIX B - Interior Signage Specification (10/2005)

APPENDIX C - Not Used.

APPENDIX D - Building Automation and Central Monitoring Systems (10/20/05) APPENDIX E - Classroom Design Standards (5/2006)

APPENDIX F - Architectural Design Guidelines (1/14/2005) APPENDIX G - Project Sign Standard (3/2006)

APPENDIX H - Networking Equipment Guidelines (1/22/2010)

APPENDIX J - Management of Refrigerant and Refrigerant Containing Equipment (2004) APPENDIX K - Carpet Procurement Specification (4/30/2008)

APPENDIX L - LEED (Leadership in Energy and Environmental Design) (4/30/2008) APPENDIX M - Fire Alarm Intersystem Interface (4/10/2010)

APPENDIX N - Site Furnishings, incl. Bike Racks (4/10/2010) 
APPENDIX O - Request for Design Approval Form (4/10/2010)

Appendix 1 – Laboratory Design Guidelines

Appendix 2 – Asbestos Free Sign Off

Appendix 3 – Site Assessment Checklist for Demolition and Renovation Projects

5

INTRODUCTION

The guidelines described in this document are for the use of architects, engineers, designers, and both in-
house and outside construction personnel. They are presented to assist the professional with the design, 
construction, and management of building projects at the Florida State University, by familiarizing him 
with  University  construction  policies  and  preferences.  The  design  professional  shall  incorporate 
applicable portions of this guide into the project drawings and specifications unless specifically relieved, 
in writing, of particular provisions by the University Project Manager assigned to his project.

This manual is divided into various sections and modeled approximately after  the Construction 
Specifications Institute (CSI) 16-division format, starting with general guidelines and site work,

continuing through architectural concerns, and concluding with engineering guidelines.

The information contained in this document is based upon sound architectural and engineering principles as well as the University's years of experience in these fields. However, these guidelines are neither completely inclusive nor totally exclusive. If a situation develops which is contradictory to these guidelines or, if the design professional can demonstrate a more advantageous solution, the University will welcome requests for modifications, upon approval by the Project Manager.

We also welcome comments and suggestions for improvements to this document to better serve the University. Questions, comments or suggestions can be addressed to Kim Strobel-Ball at Facilities Design and Construction, Facilities Design Office, The Florida State University, 109 Mendenhall Building A, Tallahassee, Florida 32306-4153 or by phone at (850) 644-2843.

REVISION HISTORY:

Beginning in the May, 2006 edition, a brief summary of major revisions will be included here, to make it 
more convenient for the user to find the most important changes. All changes to the main body of these 
guidelines, both major and minor, made since the edition immediately preceding, will be shown by a 
vertical bar in the margin. Changes to Appendices will be noted here, but may not include margin bars.

May 2006:

1.  Major formatting revision to the information previously contained in the 2/20/04 Appendix E -
	Classroom Design Standard, are included in this edition. Few changes have been made to the actual 
	classroom design requirements themselves, but, in order to facilitate spec writing, some of the 
	information contained in the previous Appendix E has been incorporated into the body of the 
	Guidelines. The user will find classroom requirements, if any, now contained in Divisions 1-16 where 
	they are related to those sections. Technology standards for classrooms and descriptions of our 
	standard classroom types are still found in Appendix E.

2.  Revised Appendix G - Project Sign Standard.

3.  Pest Control requirements have been updated and relocated to a more appropriate spot in the 
	guidelines and given a separate section under Division 2 - Site work.

April 2008:

1.  Revised  Division	2	- Sitework,  Landscaping  guidelines  and  included  design  guidelines  and

specifications for campus irrigations system.

2. 	Revised Division  4 - Masonry, paragraph 13, multiple wythe masonry construction.

3.  Revised Division 5 - Metals, Exterior Metal Stud Walls to clarify their use.

4.  Revised Division 8 - Doors and Windows, General Hardware Guidelines, Exterior Door Hardware. 
	6

5.  Revised Division 9 -Materials and Finishes,

5.1. Carpet,  Glue-Down Installation Guidelines

5.2. Acoustical Ceiling Tile, Suspension system requirements.

6.  Revised Division 10 - Specialties, General Accessory Requirements for Specific Spaces

6.1. Toilets

6.2. Custodial Closets.

7.  Revised Division 14 - Elevators Chair Lifts and Dumbwaiters, XVIII Elevator Phone.

8.  Revised Division 15 - Mechanical Utilities and Equipment

8.1. Plumbing, Paragraph 12 Urinals

8.2. Plumbing, Paragraph 16 Water Closets

9.  Revised Division 16 Electrical

10. Revised Appendix K, Carpet Procurement Specifications, Acceptable Manufacturers

11. Added Appendix L, LEED (Leadership in Energy and Environmental Design)

April 2010:

1.  Revised Division - General Planning and Design Data - Revised contact info and miscellaneous 
	administrative procedures, including as-built document requirements.

2.  Revised Division 2 - Landscaping.  Deleted Appendix C and incorporated in Div. 2.

3.  Revised Division 2 - Irrigation.

4.  Revised Division 9 - Materials and Finishes - Carpet.

5.  Revised Division 10 - Specialties -Updated toilet accessories.

6.  Deleted Carpet from Appendix and incorporated into overall guidelines.

7.  Revised Division 15 - Mechanical.

8.  Revised Division 16 - Electrical.

9.  Revised Division 16 - Electrical Fire Alarm - Interior System Interface to incorporate public address 
	microphone.

10. Revised Appendix L, LEED (Leadership in Energy and Environmental Design).

11. Revised Division 11 - Equipment - Deleted requirement for trash compacting equipment, trash 
	chutes, and trash receiving rooms.  Add requirement for recycling area.

12. Revised Division 8 - Doors and Windows - Added new review requirements for security systems and 
	card access.

13. Revised Appendix H -Networking Equipment to reflect upgrades and current practices.

14. Added Appendix M - Interior System Interface specifications.

15. Added Appendix N - Site Furnishings, incl. Bike Rack requirements.

16. Added Appendix O - Request for Design Approval Form - Added new form to document approval 
	and waivers to FSU Design Guidelines.

7

DIVISION 1 - GENERAL PLANNING AND DESIGN DATA

GENERAL GUIDELINES FOR ARCHITECTURAL AND ENGINEERING SERVICES

1.	The Architect/Engineer (A/E) shall endeavor to provide a design concept which will facilitate

possible future, changes, expansion, or renovation.

2. 	The Design Professional shall follow all requirements specified in the current edition of the 
	"Professional Services Guide". It will be the responsibility of the A/E to ascertain that the project 
	concurs with current:

a. Fire safety requirements as provided in Section 255.25(5), F.S. including required plan review by the State Fire Marshal's Office.

b. Requirements for the physically disabled as provided in Section 255.21 F.S., including the  2012 Florida Accessibility Code for Building Construction.

c. Flood plain management criteria as described in Section 255.25(6) F.S.

d. Facility energy evaluation per the requirements of Section 255.254 F.S. and Florida Building Code Mechanical and Energy Conservation.

e. Applicable codes, regulations, and orders as listed in the "Professional Services Guide.‖

f. The Project Management Section will assist and advise in these matters. Prior to commencing the preparation of schematic drawings, the design professional will be invited to participate in conferences with the University staff at which time he will be informed of more detailed requirements and specific data concerning materials, heating, air conditioning, electrical work, plumbing, and related areas.

3. 	Adequate time shall be programmed in the design process for complete review of design by the 
	University staff at the Schematics, Design Development and Construction Documents phases. At least 
	one week or preferably ten days shall be allowed for each review. Written approval of each submittal 
	shall  be  obtained  from  the  University  Project  Management  Section  before  proceeding  with 
	subsequent phases. In no case shall the design professional release construction documents to 
	prospective contractors prior to final approval of all documents by the University.

4. 	As part of the design contract the A/E shall prepare, and submit to the University Project Manager for 
	approval, two copies of the Florida Life Cycle Energy Evaluation study utilizing the Trane Trace 
	program, or approved equal, if necessary for the project. The completed study shall be submitted for 
	approval no later than the Advanced Schematics Design Phase.

5.	The A/E shall give a complete copy of this document to all consultants.

6.	The University requests that "cuts" or drawings of all lighting fixtures, plumbing fixtures and heating

and air-conditioning equipment be provided for review with the design development drawings.

7.	If required by contract or by additional services authorization, the design professional shall, using the

record set of drawings provided by the contractor, prepare and submit (1) complete set of as-built

8

drawings on acid free vellum and one set of diskettes containing complete CAD files complying with 
the CAD submittal requirements in the ―Professional Services Guide‖. These drawings must be of the 
highest quality to allow the production of clear legible prints. Unless otherwise stipulated, these as-
built drawings will be produced on sheets measuring 24" x 36". Upon completion, the A/E shall 
deliver the complete set of drawings to the Project Manager. For electrical and mechanical equipment, 
furnish three hard copy sets of operating manuals, wiring diagrams, pneumatic and electronic control 
diagrams, and parts lists applicable to each piece of equipment. Maintenance instructions and parts 
lists are to be bound in booklet form. Furnish an as-installed diagram of controls, wiring and 
operating instructions mounted behind glass on the equipment room wall for each mechanical room.

8.  The A/E shall provide to the university a set of as-built key plans drawn to scale of a minimum of 
	1"=30‘ for all new buildings or substantial renovations. Provide (1) copy of key plans on acid free 
	vellum, along w/electronic copies on one set of diskettes (current AutoCAD Version). Key plans shall 
	be drawn for production on a 12" x 18" sheet with 11" x 17" inside border, one floor per sheet. 
	Samples of existing key plans will be provided upon request.

9.  The A/E shall provide, in final specifications, for the contractor's coordination with neighboring 
	buildings or activities in cases of excessive noise, vibrations, utilities outages and the like.

GENERAL CONTRACT GUIDELINES

1. 	The contractor shall keep a set of project construction documents on site at all times and log all 
	changes made during the construction period. No deviations from the drawings and specifications 
	shall be made without full knowledge and consent of the architect or engineer. Record drawings shall 
	show dimensions, location, and depth of all buried and concealed piping, plugged outlets, and 
	equipment and shall be kept up to date. No backfilling of trenches will be permitted until the Project 
	Manager approves as-built drawings as up-to-date. Depth of sewers shall be from a permanent 
	benchmark as shown on the contract drawings. The contractor shall maintain a daily log of weather 
	conditions.

2.	The construction contract shall provide for security guards at the construction site during specified

periods on a unit cost basis.

3. 	All construction, renovation, repairs or maintenance work shall be scheduled so as not to disrupt 
	University operations at any time. The contractor, subcontractor, repairperson, or the like shall 
	schedule and coordinate all work with the University Project Manager before commencing. The 
	contractor must understand that after-hour work may be required to accomplish the work.

4. 	Damage to University property or other property incurred by the contractor during any stage of the 
	work shall be immediately reported in writing to the project manager, repaired and the damaged area restored to its original condition by the 
	contractor at no expense to the University.

5. 	Projects will only be certified substantially complete when the Project is ready for occupancy for its 
	intended use and approved for occupancy by the State Fire Marshall and the FSU Building Official.

6. 	Alternates. A limited number of alternates may be used as a means of ensuring base bids within the 
	available construction funds.   The Architect/Engineer shall consult the Owner regarding priority of 
	alternates.   Only additive alternates shall be used.   Proposals should be clearly defined, listed in 
	priority of need and held to not more than 7% of construction cost.

7. 	The Contractor shall prepare a master construction schedule using the Critical Path Method, as 
	outlined in the Associated General Contractors of America (AGC) publication "The Use of CPM in 
	Construction - A Manual for General Contractors" (An alternate type of schedule will be considered

based on the project complexity and size.)

8.	Quality control is of major importance in each university construction project. Provide requirements

for compliance (rather than simply referencing standards).   The Architect/Engineer shall provide an

9

up-to-date copy of his/her respective firm's in-house quality control manual.

9.  Project Record Documents: The Contractor shall maintain on site one set of the following record 
	documents to record actual revisions to the Work: Contract Drawings, Specifications, Addenda, State 
	Fire Marshal Approved Documents, Change Orders and other Modifications to the contract, 
	Approved Shop Drawings, product data, and samples. Record documents shall be stored separately 
	from documents  used  for  construction  and  kept  concurrent  with  construction  progress.  The 
	Architect/Engineer shall monitor and verify progress in updating record documents prior to approval 
	of Contractor's monthly Applications for Payment. The Architect/Engineer shall require submission 
	of record drawings reflecting "record set" conditions to the University with the project Close-out 
	Documents.   This "record set" shall be adequate to provide the Owner with a permanent record of 
	actual construction, to facilitate troubleshooting, and for use in future building alterations.

10. Contract Closeout Documents. At project completion, the Construction Manager shall submit (3) 
	electronic copies of all Closeout Documents.  Include copies of all completion certificates, warranties, 
	submittals, shop drawings, testing/certifications, information regarding final cleaning, adjusting, 
	Project Record Documents, close out procedures, and manufacturers‘ maintenance instructions 
	including schedules showing proper  time  intervals for lubrication,  adjustment,  calibration  or 
	checking.   Contractor shall consolidate manufacturers' schedules with a single master schedule of 
	required maintenance.

11. HVAC Systems Manuals: The Contractor shall submit to Architect/Engineer, no later than the 75% 
	completion date of the HVAC systems, four sets of manuals (or if deemed prudent, a draft set of 
	manuals) for review.   Architect/Engineer shall review and require such changes or additions as 
	necessary  to  meet  these  standards  and  when  Architect/Engineer  approves  the  manuals,  the 
	Architect/Engineer shall forward a set to the Owner.  The Owner will review and comment and will 
	advise the Architect/Engineer, who will then secure the required corrections and transmit three 
	completed sets to the Owner before a Certificate of Substantial Completion is issued.

GENERAL DESIGN GUIDELINES

General Information

1.  Adhere to the requirements of the Agreement and the ―Professional Services Guide‖ for each 
	submittal.

2.  Comply with applicable codes, regulations and orders as listed in the "Professional Services Guide".

3.  Make all contact through the University Project Manager as the "single point of contact" and 
	coordinator for all University Departments and Offices.

4.  Comply with requirements for the physically disabled and follow the ADA Requirements, and Fair 
	Housing Act where required.

5.  Coordinate  between  Architectural,  Structural,  Plumbing,  Mechanical  and  Electrical  Sections 
	concerning compliance and consistency with applicable codes.

6.  All site plan drawings shall be geo-referenced to the NAD 1983 State Plane, Florida North 0903, US 
	Foot.  This would include, but not be limited to, showing utilities (existing and new), area lights, blue 
	lights, building foot print, sidewalks, roadway/street edges, parking lots, other impervious data, etc.

7.  Provide Post-Occupancy Services as required.

8.  Upon completion of Schematic Design Phase, room numbers and door numbers shall be coordinated 
	with the FSU Office of Space Management through the Project Manager. Final numbers shall not 
	appear on subsequent documents without prior approval from the Project Manager.

10

9.  FSU prefers simplified detailing to reduce costs.

10. Endeavor to incorporate a design concept that will facilitate possible future changes, expansion, or 
	renovation.

11. Comply with fire safety requirements including required plan review by the State Fire Marshal's 
	Office and establish early reviews with the State Fire Marshal during preliminary design phases.

12. Coordinate with the Physical Plant Department and the Department of Environmental Health &
	Safety (EH&S) where toxic/hazardous materials are involved in a project and incorporate Environmental 
	Health and Safety specific requirements in Specifications.

13. Ensure that Geotechnical Engineer's analysis and site investigation data is evaluated by a structural 
	engineer and coordinated with the structural engineer's design criteria. Provide plans showing 
	required test boring locations and any other information required for the testing laboratory‘s sub-
	surface investigation. Study underground utilities and avoid them when locating test-boring locations.

14. In buildings that require laundry and vending equipment, a separate room or space must be provided. 
	Provide min (1) network drop connected to an Office of Telecommunication Integration (OTI) 
	managed switch in the telcom room.

15. Provide low maintenance and no maintenance materials and equipment both interior and exterior.

16. Don't use products containing asbestos. Upon Substantial Completion of the Project, The Architect,

Construction Manager and Contractor shall provide the Owner a Document stating that materials used in

this Project did not contain asbestos.  Use Appendix 2  Document for this purpose.

17. Follow the Florida Department of Education, State Requirements for Educational Facilities, Rule 6A-

2.0111, for space requirements and ask for written interpretation for unique spaces not shown.

18. Ensure that all proposed and expanded services and distribution systems and infrastructure are 
	coordinated with the University's Utilities Master Plan.

19. For areas that must be occupied by a specific date, coordinate and schedule time for these moves with 
	the Project Manager.

20. Thoroughly investigate and take measures to maintain services to surrounding areas that are occupied.

21. Provide temporary partitions to control dust and noise. Schedule intrusive work during off hours.

22. Provide  safety procedures for "Hot Work", especially in areas where volatile gases and fuels 
	are in use (for example medical, laboratory, and garage spaces). Project personnel should consult with EH&S prior to initiating these activities.

23. Provide specific guidance to provide for future work such as additions or installations of special 
	equipment, with particular attention to fire safety, circulation, accessibility, structural provisions, 
	utilities, site work, and future extensions of piping, ductwork and electrical service.

24. Specify method of payment for water, fuel, chilled water and power consumed by the Contractor. 
	Require the general contractor to make arrangements, through the University Project Manager, with 
	the Department of Physical Plant for installation of temporary lines.

25. Operation and Maintenance Data. Provide detailed requirements in the appropriate sections of the 
	specifications.   The following checklists should be modified to suit project requirements: Roofing 
	Manufacturers maintenance data. Elevators and hoists as per specifications. Piping systems (printed 
	diagrams,  valve  tag,  etc).  Control  systems (printed  diagrams,  operating  instructions,  etc).

Communications 	(point-to-point wiring diagrams and instruction manuals, if installed by the

Contractor). Fire protection systems (as per specifications). Motor control (overload heater charts). Equipment (operating instructions).

26. Project  Turnover  Procedures.  Specify  instructions  and  requirements  of  the  Contractor, 
	Architect/Engineer and Owner for acceptance of the project.   The Architect/Engineer is responsible 
	for including in the Specifications the obligations for the Contractor, for an orderly acceptance and 
	turnover. Included in such obligations are: punch lists, "record set" plans and specifications, operating

11

and maintenance manuals, and indoctrination of the university personnel.  Include written notification for insurance purposes.   Include a requirement that all submittals, shop drawings, warranties, and close out documents be scanned to archival quality disks for incorporation into the University‘s electronic archives.

Visual Clutter

1.  Certain building system components are typically visible on the exterior of a building or elsewhere on 
	a project site. These components, which include devices such as backflow preventers, transformers, 
	switchgear, condenser units, and waste dumpsters, detract from a building‘s appearance if not 
	appropriately handled. The design professional shall exercise care to ensure that these types of 
	devices do not impact or detract from the project‘s appearance. Ideally, the device shall be 
	incorporated into a project‘s design in such a manner that it is not conspicuous. Other types of 
	concealment, such as screening walls or landscaping, shall be utilized where appropriate. All methods 
	of concealment must comply with all applicable codes and with the access requirements of local 
	utilities.

Acoustical Treatment

General Requirements

Proper control of sound is essential to the function of an educational environment such as FSU. Pursuant 
to this fact, the Design Professional shall determine, in conjunction with University representatives, 
appropriate sound control characteristics on a space by space basis and provide acoustical privacy from 
space-to-space consisting of, but not limited to, (1) partitions full height up to the underside of structure 
above (not up to suspended or dropped ceilings), (2) carpeting, acoustical ceilings and other sound 
absorptive surfaces as appropriate to the use and maintenance of the space, (3) protection of openings 
such as solid core wood stave doors with sound seals, (4) control of ambient noise and (5) other measures 
required to accomplish sound control goals for each space, as set forth by University representatives and 
these guidelines.

Specific spaces that will always require sound control measures shall be, but are not limited to, the 
following: offices, interview rooms, conference rooms, classrooms, seminar rooms, and lecture halls. 
Consideration shall be give at the early planning stages of a project to the location of sound sensitive 
spaces in relation to spaces that are sources of ambient noise, such as mechanical rooms, lobbies, break 
rooms, food service areas, loading docks, elevator shafts, restrooms, trash disposal areas, outdoor areas 
where people gather, high traffic outdoors areas, and nearby noise producing equipment such as 
generators. Where site conditions and other planning considerations make it necessary to locate sound 
generating functions near those with sensitive sound control requirements, special consideration shall be 
given to the separation of these functions with effective sound transmission barriers.

Acoustical Treatments for Classrooms

1.  To prevent noise transmission, there should not be a common wall or ceiling between any classroom 
	or lecture hall and the restrooms.   If that is unavoidable, then additional measures must be taken to 
	prevent noise transmission.

2.  Classrooms shall be located away from sources of high noise levels (e.g., mechanical rooms, elevator 
	shafts) as noted above.

3.  Structural columns and other obstructions shall not be placed within the seating areas of classrooms 
	and lecture halls, so as not to obscure sightlines to the instructor or projected images. In renovations, 
	the Design Professional should avoid laying out classrooms such that structural columns are within 
	the seating area.  If that is absolutely unavoidable, then the Design Professional should consult with 
	University representatives on ways to minimize the impact of such columns.

12

4.  Corridor walls (or common walls with other unsecured rooms) shall run from floor to underside of 
	structure above.   Special consideration should be given to wall or partition construction above the 
	ceiling lines on the corridor side of the room.

5.  Walls in classrooms and lecture halls should have a minimum sound transmission class (STC) rating 
	of 50.  All walls must extend to the floor above or to the roof construction, and not stop at the ceiling. 
	(This reduces noise transmission as well as improves security.)

6.  Higher STC ratings and special wall-construction details must be included whenever classrooms are 
	located adjacent to, above, or below restrooms, mechanical rooms, elevator shafts, bus stops, athletic 
	facilities, or other sources of high noise levels, or where the classroom function generates a 
	significant amount of noise (e.g., a music classroom).

7.  The mechanical system supporting general-purpose classrooms should generate a background noise 
	level of no more than NC 35 (preferably designed to NC 30), and should provide at least six changes 
	of air per hour with an NC (Noise Criterion) rating less than 30.  Ducts need to be sized large enough 
	to permit low air velocities.  Select diffusers with NC ratings below 25.  Design longer duct runs to 
	reduce mechanical noise and reduce the transmission of sound between classrooms.    Locate 
	mechanical equipment away from classrooms.  Other suggestions may be found at www.ashrae.com. 
	Ambient sound levels measured at 48‖ AFF at all points throughout the room should have a Noise 
	Criterion (NC) rating of no more than 35 (preferably 30).  Background noise should not exceed 45dB-

C.  Although the space should be designed to an NC of 30-35, it does not have to be certified. 	(FSU

reserves the right to certify a random sample of rooms to ensure that this standard was met.)

8.  For specific requirements of each standard FSU Classroom Type - see Appendix E.

Accessibility Guidelines

1.  All renovations and new work shall meet the requirements for the physically disabled as 
	described in Section 255.21, Florida Statutes, American with Disabilities Act, OSHA, and ANSI.

2.  The presence of many visually and physically disabled students on campus must be taken into 
	consideration in preparing construction documents.

3.  Outside stairways shall have railings as required by OSHA and as modified by the latest ANSI 
	standards for the handicapped.

4.  Any raised platforms shall have railings, toe-boards, labeling, and painting and shall conform to 
	OSHA requirements as modified by ANSI standards for the handicapped.

5.  Should the A/E team recommend a design solution which requires an accessibility waiver from 
	any public agency, the A/E shall be responsible for preparation and presentation of all related 
	documents.

6.  All new buildings shall include provisions for at least one accessible push button door operator. 
	This operator should be located at the main building entry and accessed by an accessible route.

7.  All tactile warning devices should be fabricated integral to the construction materials.   All 
	warning materials should be of contrasting colors.   Cementitious materials are preferred at curb 
	cuts.  Provide warning materials constructed of 8000 psi concrete to prevent chipping at corners

and edges. No mechanically fastened mats will be allowed.  Color for tactile warning material at curb cuts shall be equal to U4008ADA as manufactured by Wausau Tile Inc.  Contrasting border materials should be provided to aid visual discrimination.  Contrasting color shall be equal to U-
1008ADA also by Wausau Tile, Inc.

13

Guidelines for Toxic/Hazardous Materials

Based on the Florida State University EPA and DEP permits for hazardous materials management 
and disposal, the following basic guidelines are provided:

1. 	The Florida Department of Environmental Protection has determined that regulated small and 
	large quantity generators of hazardous waste are responsible for all hazardous wastes generated 
	on their sites. Therefore, contractors working on the campus must comply with the same federal 
	and state regulations pertaining to hazardous waste management and disposal as the University.

2. 	Based on the Florida State University EPA and DEP permits for hazardous materials management 
	and disposal, the following basic guidelines are provided:

3.	On main campus all hazardous wastes are required to be collected, managed and disposed of from

the construction location.

4.	Other campus location programs must be determined at the time of the construction activity.

5. 	Appropriate laws must be followed at all times for the use, collection and disposal of all 
	hazardous materials. Contact the University Department of Environmental Health & Safety (EH&S) for additional information (644-6895).

6. 	The A/E shall complete an environmental assessment survey as specified in the Site Assessment Checklist for Demolition and Renovation Projects (Appendix 3) The A/E, contractor and other related safety 
	personnel should contact EH&S 
	concerning all questions, comments or instructions on all toxic/hazardous materials involved in a 
	project.

7. 	Prior to contracting for work, each contractor, subcontractor, and their employees, who use 
	hazardous materials and may generate a hazardous waste, must provide evidence to the University of having 
	received RCRA (Resource, Conservation & Recovery Act) Hazardous Waste Awareness Training 
	and Hazardous Materials Emergency Response Awareness Training as required by 29 CFR 
	1910.120 and 40 CFR 311.

8. 	All construction, maintenance, and/or investigative work shall be coordinated with the Facilities 
	Planning and Construction Department and EH&S 
	where toxic/hazardous materials are involved.

9. Materials shall be selected to minimize hazardous material (lead, chromium, etc.) use during the 
	project. Any building material containing a hazardous material shall not be specified or used in a 
	building project, unless specifically approved by the Project Manager and EH&S. No material containing asbestos may be specified or 
	used in a building project, as provided by Section 255.40, F.S. No materials or equipment containing 	polychlorinated  biphenyls (PCB) shall be used in new construction or renovation as provided by EPA 40  CFR Part 761.  Use of lead pipes, solder and flux, is prohibited in new construction and renovation as provided by EPA 40 CFR 141.113.

10. All electrical transformers, switches, or other electrical equipment which contains polychlorinated 
	biphenyls (PCB) or other equipment which has come in contact with PCB is to be identified and 
	brought to the attention of the University Project Manager and EH&S. Under no 
	circumstances is the contractor, subcontractor or other related personnel allowed to remove such 
	equipment off the site without prior approval of EH&S. The A/E shall contact the University 
	Project Manager and EH&S regarding handling 
	procedures of this equipment.

11. Any hazardous or toxic material, such as asbestos, lead based paint or PCB, which is discovered 
	during the course of a project, shall be reported immediately to the University Project Manager. 
	All work involving suspected asbestos, hazardous, or toxic materials shall halt immediately and 
	shall not resume until a notice to resume work has been given by the Project Manager.

12. The A/E shall contact the University Department of Environmental Health and Safety prior to the 
	commencement of a renovation project in order to determine the extent of asbestos containing materials or other

14

hazardous materials in a particular building.

14. In order for the environmental design engineer to be able to submit the final asbestos/lead 
	abatement report to the University Department of Environmental Health and Safety in a timely 
	fashion (60 days after substantial completion), the abatement contractor shall provide post project 
	submittals within 14 calendar days after substantial completion.

GUIDELINES FOR EMERGENCY USE & STRUCTURAL MITIGATION

- The Department of Environmental Health & Safety, Emergency Management Section, maintains an overarching Mitigation Plan for ensuring that all new or renovated structures consider measures that ensure safety and resiliency.  Some types of structures may be targeted for structural enhancements to allow the facility to be utilized during an emergency; and/or to ensure structural survivability and continuity.  The Department of Environmental Health & Safety, Emergency Management Section serves as the official liaison with Leon County Emergency Management, City of Tallahassee Emergency Management and the Florida Division of Emergency Management and should be consulted prior to the design phase of each project to ensure that such enhancements are not needed.

- Pursuant to section 252.38(1) (d), Florida Statutes, all educational facilities, including state universities, are to be considered for use as emergency shelters.  Section 1013.74(4) Florida Statutes, “the university board of trustees, in consultation with local and state emergency management agencies” shall ensure that “new or retrofitted facilities will incorporate enhanced hurricane resistance standards and that can be used as public hurricane evacuation shelters.”

- The Enhanced Hurricane Protection Area (EHPA) requirements outlined in section 1013.372 Florida Statutes may be waived in certain conditions.  One such condition is the existence of a hurricane shelter space surplus within the region.  Regardless of the existence of said regional surplus for public use, the Department of Environmental Health & Safety, Emergency Management Section shall be consulted to ascertain the need for such space to meet on-campus needs for students, faculty, staff, and families thereof..

- The university shall consider opportunities for other structural enhancements or mitigation that will ensure the survivability of the facility against the identified hazards of the institution.  Such enhancements may include, but are not limited to:  enhanced wind design, impact-resistant doors and windows, flood-proofing, security enhancements, emergency power, and other life-safety systems.  Such enhancements are intended to minimize structural damage from a hazard, ensure that the facility can continue to function, and/or return to prompt functional use.  Certain types of facilities are deemed “critical facilities” that require measures to ensure resilience and continuity. The Department of Environmental Health & Safety, Emergency Management Section shall be consulted to ascertain the need for such enhancements or mitigations. External grant funding may be available to accomplish such projects if consulted far enough in advance.

DESIGN CRITERIA FOR SPECIFIC SPACES

Design of Parking Structures

Special attention must be paid to the location and design of Parking Structures, conformity to the Master 
Plan, ingress and egress, traffic control, vehicular and pedestrian circulation, utilities and services, safety 
and  security systems,  code  conformance,  provisions  for the  handicapped, signage,  lighting,  and 
protection.  Special attention must also be paid to the selection of the structural system and materials, the 
design and location of control and expansion joints, sealants, treatment of parking surface, finishes, and 
underside of structure, slopes (minimum of 1/4" per foot), location and design of drains, gutters,

waterproofing systems and membranes to avoid water penetration and material deterioration, and maintenance and operation programs.

Restroom Design

1.  Restrooms for men and women must be supplied on each floor. All restrooms are to be sized and 
	equipped for the handicapped in accordance with the 2012 Florida Accessibility Code for Building Construction. Public 
	restrooms in residence halls are only needed at the main lobby and/or the building recreation room.

2.  Countertops and shelves shall comply with Division 6 requirements.

3.  Restroom doors shall comply with Division 8 requirements.

4.  Floor finishes shall comply with Division 9 requirements.

5.  Fixtures and partitions shall comply with Division 10 requirements.

6.  Toilet room accessories shall comply with Division 10 requirements.

7.  Restroom lighting shall comply with Division 16 requirements.

8.  Provision of push button operators at doors shall be per current code requirements.   Installation of 
	push button operators beyond those required by code shall be discussed on a case-by-case basis in 
	coordination with the University ADA Coordinator.

Classroom Design

1.  Classrooms shall be located on the lower floors to minimize the amount of traffic that uses elevators 
	or stairways.

2.  Classrooms should be protected from noise generating spaces such as stairwells, elevator equipment 
	rooms, loading docks, and lobby areas.

3.  Restrooms shall be located on each floor, and the capacity of the restrooms should be calculated 
	according to the number of students in the area during class change times rather than according to the 
	capacity of the classrooms.

4.  Structural columns and other obstructions shall not be placed within the seating areas of classrooms 
	and lecture halls, so as not to obscure sightlines to the instructor or projected images. In renovations, 
	the Design Professional should avoid laying out classrooms such that structural columns are within 
	the seating area.  If that is absolutely unavoidable, then the Design Professional should consult with 
	University representatives on ways to minimize the impact of such columns.

15

5.  In new construction, ceiling height shall be a minimum of 10'.   The larger the room, the higher the 
	ceiling should be.   Ceiling height must be determined based on the height of the projected image, 
	which is 1/6th the distance of the farthest student from the projection screen.  To that dimension, add 
	48‖ (e.g., in a room in which the farthest student sits 54‘ from the projection screen, the height of the 
	projected image will be 9‘, to which 4‘ will be added making the ceiling height at the front of the 
	room 13‘).  (See also notes regarding ceiling height in lecture halls.)  For renovations, in no case shall 
	the ceiling height at the front of a classroom be lower than 9‘.

6.  Classrooms shall be designed to maximize the seating capacity.   This would include placing the 
	entrance at the front of the room.

7.  The front wall of the classroom shall be clear of any protrusions or light switches or thermostats or 
	fire-alarm enunciators so that a marker board may be installed across the entire front wall.

8.  Dry-erase marker boards shall be used instead of chalkboards. See Division 10.

9.  Instructor consoles shall be located so as not to obscure the students' sight line of the projection 
	screen(s) and marker board(s).

10. For lighting requirements specific to classrooms, see Division 16.

11. There should be no elevator motors, compressor motors, blower motors, or other types of equipment 
	on the side of the power transformer that feeds classroom or lecture hall circuits.

12. Power poles shall not be used within a classroom.

13. Folding walls must not be used in classrooms because it is difficult to have a folding-wall design that 
	will maintain adequate sound separation between classrooms over an extended period of time.

14. All classrooms with permanently installed multimedia equipment shall be connected to a security 
	system.  The security system shall include a card access reader at the main entry door, door security 
	contacts on each door and motion sensors in the room.  The panels for the security system shall be on 
	emergency power circuits.

15. The lower portion of the corridor walls in classroom areas should have a very durable surface to 
	protect walls and corners from the heavy traffic found during class change times.   This protection 
	should extend to approximately shoulder height to protect against damage from backpacks.

16. A high-density plastic chair rail shall be placed on the side walls surrounding the seating area.

17. Audio-visual Requirements - see Appendix E.

18. For specific requirements of each standard FSU Classroom Type - see Appendix E.

Custodial Closet Design

1.  Provide a minimum of one custodial closet with sink on each floor. Tool holders shall be mounted 
	above the sinks for wet mops. Minimum floor space to be 6'-0" x 8'-0"

2.  Custodial closets shall not share space with building mechanical, plumbing, electrical, or telephone 
	equipment and shall not be a passageway to such a room. They shall be directly entered from a 
	corridor.

3.  The closet assembly shall conform to the current NFPA Fire Marshal requirements.

4.  Provide a central custodial/storage area on the ground floor with similar features to the standard 
	closets except increase area size to approximately 225 square feet and provide additional shelving. 
	This room shall be easily accessible from the building central delivery point.

5.  Comply with door and hardware requirements in Division 8. 
	16

6.  Comply with finish requirements in Division 9.

7.  Comply with requirements in Division 10.

8.  Comply with plumbing fixture requirements in Division 15.

9.  Comply with lighting requirements in Division 16.

17

DIVISION 2 - SITEWORK

AESTHETIC COMPATIBILITY

1.  Refer to the University‘s Architectural Design Guidelines, Landscape Design Guidelines and Campus 
	Beautification Standards for guidance in these matters.

2.  The use of chain link fences shall be kept to a minimum, but where their use is required; the entire 
	fence system shall conform to ASTM F669 Heavy Industrial Fencing, with ASTM Medium Industrial 
	wire fabric, black PVC coated per ASTM F668.

3.  Ensure that Project Site is coordinated with Master Plan criteria.

GENERAL GUIDELINES

1.  Provisions shall be made for locating a dumpster receptacle and recycling containers in an accessible 
	site with aesthetic screening provided.

2.  The building shall have at least one loading zone to accommodate frequent moving of portable 
	equipment to and from the building and to allow maintenance vans and personnel to have ready 
	access to the building. Where loading docks are provided, they shall be located as close as possible to 
	freight/passenger elevators and shall be covered.

3.  All parking and spaces used outside of the construction area will require that decals be purchased 
	from the University Parking Services Department, except for construction vehicles with the 
	contractor‘s logo on them.

4.  The contractor will determine the number of special entrance permits that are required and will 
	submit a request for these permits to the Project Manager.

SAFETY PROVISIONS, SECURITY PROVISIONS AND TEMPORARY SERVICES DURING CONSTRUCTION

1.  A six-foot high heavy woven steel wire fence on steel posts (where appearance is a consideration, a 
	privacy type fence might be required) with gates shall be erected around the project site. No 
	trespassing signs to meet OSHA requirements shall be specified. The fence shall be shown on the 
	drawings. The University shall be held harmless if improper or inadequate fencing is installed by the 
	Contractor and injury or damage results.  Considerations for student and pedestrian safety are a must. 
	Review the location of fencing, entry gates, and use of fabric screen with the Project Manager.

2.  Building Security:   Provide one exterior door of any enclosed structure with a lockset including a 
	university security cylinder during construction. Furnish the University Project Manager two keys for 
	each lock or two masters for all gate locks.  These keys will be turned over to the University Police 
	Department for emergency access to the construction site.

3.  Safety of Persons and Property:  The Contractor shall take precautions for the safety of, 
	and shall provide all reasonable protection to prevent damage, injury or loss to all university faculty, 
	staff, and students and all other persons who may be affected. This protection also extends, to all  completed work, all materials 
	and equipment to be incorporated therein, whether in storage on or off the site, under the care, 
	custody or control of the Contractor or any Subcontractors or Sub-subcontractors. Other property at 
	the site or adjacent thereto, including trees, shrubs, lawns, walks, pavements, roadways, structures 
	and utilities not designated for removal, relocation or replacement in the course of construction.

4.  When the use or storage of explosives or other hazardous materials on campus is necessary for the 
	execution of the work, the Contractor shall exercise the utmost care and shall carry on such activities

18

under the supervision of properly qualified personnel.   Notification of such activities shall be provided to the University Project Manager and the University Department of Environmental Health & Safety (EH&S) prior to their being brought and/or used on campus.

5.  The specifications shall require the Contractor and its employees, while working on the premises, to 
	comply with the Safety Orders issued by OSHA, the University Director of EH&S and any other safety, health or environmental regulations of the State of Florida having 
	jurisdictional authority.

6.The contractor and all subcontractors shall comply with all applicable OSHA standards.  Upon request by the Project Manager the contractor or subcontractor shall provide proof of compliance to include personnel training records.7.  The Contractor shall designate a responsible member of his organization at the site whose duty shall 
	be the prevention of accidents.  This person shall be the Contractor's superintendent unless otherwise 
	designated by the Contractor in writing to EH&S  and the University Project Manager.

8.  The Contractor shall not load or permit any part of the work to be loaded so as to endanger its safety.

9.  In any emergency affecting the safety of persons or property, the Contractor shall take appropriate action to prevent damage, injury or loss.   Immediate notification of such occurrences must be 
	made to the University Police Department and the Project Manager .

10.  The  specifications  shall  require  that  no  persons,  other  than  employees  of  the  Contractor, 
	Architect/Engineer, FSU Facilities Department, FSU EH&S, or FSU Office 
	of Telecommunications enter the construction work site without specific prior approval of one of 
	these parties.  Warning signs may be posted to assist in the enforcement of this requirement.

11. The Contractor shall provide continuous utility services until the date of Substantial Completion, or 
	Beneficial Occupancy, whichever comes first, including operation of permanent equipment and 
	services.

12. Provide temporary heating and cooling as necessary to protect the work from dampness and cold, and 
	to dry out the building prior to millwork doors, paint and acoustical tile installation.

13. Provide  temporary  water  necessary  for  construction,  drinking,  and  testing  of  plumbing  and 
	mechanical systems from the department of Facilities, Utilities Section through the University Project 
	Manager.   The connection point must be verified by the Utilities Section. The line size must be 
	adequate for all demands.  Make necessary connections and install a meter, and install all pipes from 
	the meter. Remove temporary lines upon job completion. All costs, including use and connection 
	fees, shall be paid by the Contractor at current rates.   All temporary water lines will have backflow 
	preventers.

14. Provide temporary Sanitary Facilities and maintain in a neat and sanitary for the use of the 
	Contractor's employees as necessary to comply with the regulations of the State Board of Health, Florida Building Code and 
	the county and municipality.  The point of tie-in to sewage systems, if utilized, shall be designated by 
	the University's Project Manager; otherwise, the Contractor shall provide adequate chemical portable 
	sanitary facilities for Contractor's forces.   Chemical toilets will not be emptied in the university 
	sewage system.  Pit toilets are prohibited.

15. Provide temporary, as well as permanent, fire protection facilities including fire hydrants.   During 
	construction, fire hydrants shall be installed within the specified distance of a building according to 
	the occupancy classification to meet the NFPA requirements that pertain thereto.

16. Provide temporary Barriers and Enclosures. The Contractor shall provide rigid barricades, especially 
	for open trenches and excavations, shielding, and/or warning signs including audible warning devices 
	for the sight impaired, to protect all University employees, students, and the general public from 
	hazards outside the required construction site fence.   This includes but is not limited to: open

19

trenches, falling objects, and the lighting and posting of warning signs about physical hazards during darkness to comply with all OSHA Standards.

17. Noise and Dust Control:  In occupied buildings, indicate areas for which noise and dust control must 
	be provided and specify  methods of control.  If details of installations are involved, specify these in 
	the applicable sections of the technical specifications.   The Contractor shall be required to install 
	barriers indicated by the Architect/Engineer and shall provide other dust control barriers as required 
	by construction operations.

18. Clean-up Enforcement:  The specifications shall contain provisions complying with the NPDES, that the Contractor must prevent and remove 
	mud and spillage from public and university streets without delay.  Failure to clean streets promptly 
	could result in streets being cleaned by the Owner at the Contractor's expense.

19. All catch basins and storm drain lines in the vicinity of the site shall be protected at all times from the 
	entry of mortar, concrete spoil, dirt and other construction debris.  The residue from the cleaning of 
	concrete trucks, wheelbarrows, concrete buggies, etc., must be prevented from entering the drainage 
	system.   If cleaning is done, it must be contained and the Contractor must remove the residue from 
	the campus with other construction refuse.

20. Repairs of Damages to Facilities:    The specifications shall contain provisions that damage to roads, 
	facilities, landscaping, hardscape, site furnishings, or other facilities and infrastructure on the 
	grounds, resulting from Contractor's hauling, storage of materials, or other activities in connection 
	with the Work, shall be repaired or replaced, at no expense to the Owner.   Repairs or replacements 
	shall be made to the Owner's satisfaction.   Clean up of areas shall occur on a weekly basis. 
	Contractor shall not overload vehicles with material causing spillage and possible future damage.

21. Planning for Temporary Control:   Specify that the University Security/Parking Services must be 
	notified at least 1 week in advance of any anticipated work affecting traffic flow.   To ensure

maintenance of flow and to safeguard all parties involved in planning temporary routing, a field inspection should be made jointly by the Architect/Engineer, the Owner, and Contractor prior to performing any work that would interrupt normal traffic patterns.   Rerouting of traffic shall be planned, as to route and direction, in cooperation with the Police Department.

22. Temporary lanes shall be well marked, and obstructions, barriers, lane changes, or detours shall be 
	indicated by appropriate signage at each point of potential confusion, as well as at each change in 
	direction of a temporary route.  The University Police Department shall be notified in advance of the 
	anticipated time of return to normal traffic patterns.   Upon completion of construction affecting 
	streets or traffic flow, but before temporary control devices and lane markings are removed, the area 
	shall be restored to receive traffic in the normal pattern.  The Police Department shall be notified of 
	the actual time of completion of restoration.

23. Project Identification and Signs. Include requirements for temporary project identification and 
	informational signs required during construction, and removal at completion of work been.  Refer to 
	Appendix G - Project Sign Standard for specific construction signage details.

24. Contractor's Office shall be of size suitable for the use of the Contractor, Subcontractors, and the 
	Architect/Engineer's representative.   Office shall be heated, lighted, and provided with doors with 
	locks, and private line telephone service.  One lockable space in the office shall be provided for use of 
	the Architect/Engineer's representative; space shall be equipped with plan table, desk, suitable chairs 
	or stools, plan rack, filing cabinet, and telephone.   The Contractor or an authorized agent shall be 
	present at the office or shall arrange to be called readily, at all times while the work is in progress.

20

PARKING

1.  The Director of Parking & Transportation Services prior to the production of final construction 
	documents and bidding the work must approve all parking lot design and designation of parking 
	spaces. Phone 850-644-5278.

2.  Address parking by including parking requirements as part of facility design and cost as well as 
	restoration of displaced and disrupted parking.

3.  All parking spaces shall comply with applicable code regulations and be a minimum of 9 feet wide.

4.  All faculty and staff parking lots shall include traffic control gates at the entrance and exit of the lot. 
	All gates shall be equivalent to Federal ADP gates.

Striping of all lots must be done using set-fast water borne traffic marking paint. Colors: TM226 White, TM2132 Red, TM2159 Yellow and TM2133 Blue. (Sherwin Williams numbers)

5.  Provision of set aside spaces for fuel efficient vehicles shall be discussed with the Project Manager.

6.  Refer to Appendix O for Bike Rack standards.

DIVISION 2 - SITEWORK

DEMOLITION

1. 	Include the removal of all structures interfering with new construction in the demolition plans. Debris 
	resulting from stripping and demolition operations shall be removed from University property at 
	frequent intervals so as to prevent this material from accumulating on the site.

2.	Authority to remove trees must be issued in writing by the Grounds Department.  This action shall be

coordinated by the Project Manager.

3. 	Removal of trees and shrubs shall include the removal of stumps and roots to the extent that no root 
	greater than three inches in diameter remains within five feet of an underground structure or utility 
	line or under footings or paved areas.   Grubbing in open areas shall include removal of stumps and 
	three-inch roots to two feet below finish grade elevations.

4. 	In open areas, foundations of structures shall be removed to a minimum of three feet below finish 
	grade elevation.  Where new structures will replace existing structures, indicate extent of foundation 
	removal on the drawings.   No existing slabs will remain under fill for new structures.   Hazardous 
	material removal shall be conducted prior to structural removal as required by federal, state and local 
	requirements.

5. 	All trees and landscape material being demolished/removed shall be hauled to the FSU Nursery site to 
	be mulched by Grounds staff for use in University landscape beds.

6. 	Disposal of existing buildings and structures, dismantled equipment, etc., is the responsibility of the 
	Contractor.  For all LEED projects, disposal of construction materials should be diverted for recycling 
	to the greatest extent possible.

7. 	Identify cutting and patching in detail, including incidental cutting, fitting, and patching required to 
	complete the work or to make several parts fit together properly.

8. 	Materials and Equipment. Salvage on Demolition and Renovation Projects. On all projects involving 
	demolition and/or renovation, the Architect/Engineer should review with the University Project 
	Manager (for inclusion in the bid documents) the possibility of salvage of materials and equipment,

21

either for use in the remodeling project, or by the Department of Physical Plant.   The University Project  Manager,  upon  notification  by the  Architect/Engineer  of  salvage  not  needed  in  the remodeling, will notify the Architect/Engineer of materials and equipment to be removed by the Owner or to be turned over to the Owner by the Contractor.    The University reserves the right to remove salvage prior to start of construction, and, in certain instances, to require the Contractor to turn over certain items of salvage.

Note: The Contractor will remove non-reusable materials, including toxic and/or hazardous waste, from campus in accordance with all applicable EPA, DEP and DOT  laws and regulations. EH&S personnel must be contacted to assist licensed brokers with document preparation, and to approve and sign hazardous waste and shipping manifests. Copies of all hazardous material related shipping documents must be forwarded to EH&S for record-keeping.

EARTHWORK

9.  No excavation, drilling, exploratory work or installation of fence posts, etc., is permitted until the 
	Contractor and university personnel review drawings of existing utility lines. Any damage done to 
	known lines shall be repaired immediately in a manner acceptable to the University and at the 
	Contractor‘s expense.

10. Earthwork includes, but is not necessarily limited to the following: excavating, filling, backfilling, 
	grading and compaction. Dewatering of excavations and work areas, as required. Shoring and 
	bracing, as required. Disposal of excess and unsuitable excavated materials. Preparation of sub-grade 
	for building slabs, walks, decks and pavements. Backfilling of trenches within contract limit lines. 
	Excavation and backfill required in conjunction with underground mechanical and electrical utilities, 
	and buried mechanical and electrical appurtenances is included as work of this section. "Excavation" 
	consists of removal of all material encountered to sub grade elevations indicated and subsequent 
	disposal of materials removed.

11. Earthwork for Buildings:   The site for the new building will be stripped and the area around the 
	existing buildings graded to suit the architectural requirements.  Excavation and removal of materials 
	from the premises will be done as required for the building and structures.  This will include disposal 
	of  debris  and  waste  material,  foundation  drainage,  backfill,  compaction,  shoring,  sheathing, 
	temporary protection and barricades.  Storm water drainage will be controlled during construction of 
	the project.   Fill as required for rough grading elevation.   Site preparation for building according to 
	Geotechnical Engineer's recommendations.

12. Earthwork:  This area should address excavation, filling and grading for the new structure as required 
	to suit site appurtenances.  Grading and filling will be performed to lines and grades required by civil 
	engineering.   These grade lines will be integrated with the new paving and surfacing as well as 
	landscaped areas.   Removal of the unsatisfactory or deleterious materials from the premises will be 
	done as required for the work.  Disposal of debris and waste material, temporary protection of work, 
	barricades, rerouting requirement, signage, etc. will also be included.   Storm water drainage will be 
	controlled during construction of the project and will also be included.

13. Rough Grading:   Slopes shall not be greater than one vertical to six horizontal in grassed areas, 
	including stormwater facilities (side slopes).   Steeper slopes will only be considered in unique 
	circumstances and must be reviewed and approved by the Owner.

14. Excavating:  The excavation and backfilling of trenches, etc., for piping, manholes, pull boxes, etc., in 
	the mechanical trades is considered better placed under those divisions than under this general 
	division but the Architect/Engineer should ensure that the compaction of backfill in trenches is 
	covered and that the soil type is the same and that restoration has occurred.

15. Under no circumstances shall topsoil and other excavated soils be removed from the campus.  If such 
	materials are not required for the project, the Contractor should consult with the University Project 
	Manager who will advise the Contractor regarding a disposal location.

16. Where topsoil is removed and grading is accomplished on the site, or where the existing ground 
	surface is otherwise disturbed, care shall be taken to prevent soil erosion.   If soil is needed, specify 
	that the Contractor will have to obtain it from private sources at the Contractor's expense.

22

17. When necessary to hold large piles of excavated earth on the job site, the Contractor should be 
	required to provide cover or adequate means of water sprinkling to keep the sand particles wet and 
	prevent them from being wind-blown about the campus.

18. Backfilling is required at building perimeter and site structures up to sub grade elevation. Fill under 
	interior and exterior slabs-on-grade or pavement, and fill under landscaped areas shall meet applicable 
	ANSI/ASTM standards.

19. Trenching. When excavating and backfilling for the mechanical and electrical trades is covered in this 
	portion of the specifications, make certain that the compaction of back-fill is properly specified and 
	meets applicable ANSI/ASTM standards and the requirements of Section 553., Part III F.S., the Trench 
	Safety Act.

PEST CONTROL

1.  New buildings should have lockable access doors installed in chases to facilitate application of 
	chemicals to prevent infestation of household pests.  Access doors shall match or exceed the rating of 
	the wall systems in which they are installed.

2.  Termite treatment is required for every building. The Subcontractor, for soil poisoning, must furnish a 
	service agreement stating the work performed will be guaranteed for a period of 5 years from the date 
	of substantial completion. In addition the agreement must state that the structure will be inspected 
	yearly for infestation and treatment provided as necessary. The Subcontractor shall offer an optional 
	renewal of the service on the same terms. The type of chemical treatment must be specified, including 
	the amount of application per unit area. The service agreement shall state that in the event of damage 
	during the guarantee period, the Contractor shall make repairs to structurally damaged surfaces to a 
	dollar value based on the size of the building, the value of which shall be coordinated with the Project 
	Manager at the time the GMP is developed. An independent testing laboratory shall certify that the 
	treatment meets the requirements of the Specifications.

3.  If treatment is provided prior to substantial completion, the Architect/Engineer should specify 
	modification of service and guarantee so that the university is not billed prior to acceptance of the 
	building.

4.  Chemicals and application shall conform to EPA's Federal Insecticide, Fungicide and Rodenticide 
	Acts.

UTILITY WORK

1.  Connections to Existing Utilities. If connections to university utilities are permitted, the specifications 
	shall require the Contractor to make requests for utilities service through the University Project 
	Manager.  Contractor shall make all necessary arrangements for the service, including the point of tie-
	in, times permitted for utility work, shutdown scheduling, traffic control, amount of lead time 
	notification, etc., with the Department of Physical Plant through the University Project Manager.  The 
	Architect/Engineer shall obtain drawings of existing utilities and shall consult university personnel 
	regarding services available and points of connections to services.   All services shall be metered 
	through meters furnished by the Contractor, and the Owner shall be reimbursed for utilities.

2.  Detectable or non-detectable plastic marking tape shall be installed underground above all buried 
	utility lines; to facilitate the location of the lines before damage to the lines can occur during required 
	excavation.

3.  Ensure that all proposed and expanded services and distribution systems and infrastructure are 
	coordinated with the University's Utilities Master Plan.

4.  Water Distribution System. Water main materials: ductile iron pressure water pipe and PVC pressure 
	23

pipe, joints are optional.  Provide gate valves at all new branches, fire hydrants, backflow prevention 
devices and meters.  Discuss valve location and installation details such as valve boxes, direct burial, 
and ground level access to valve operator with the university.   Water lines will be disinfected 
according to AWWA Standard C-601.   All pipes will be tested for leakage.   Detectable plastic 
marking tape shall be installed underground above buried utility lines, as required; to facilitate the 
location of the lines before damage to the lines can occur during required excavation.  All piping shall 
be protected from freezing.

5.  Sanitary Sewer System. Sanitary sewers shall be vitrified clay pipe with gasketed push joints or PVC 
	pipe with joints as recommended by pipe manufacturer.  Sanitary manholes shall be precast concrete 
	or cast-in-place concrete.   Cover and frames shall be cast iron. Cleanouts shall be commercially 
	manufactured wye branches.

PAVING

1.	All exterior ramps, stairs, landings and walks shall have an integral non-slip finish and provided with

a waterproof sealant coating.

2. 	Expansion joints shall be provided in all concrete sidewalks every 20'-0" regardless of width. The 
	expansion joint shall be made of elastomeric pre-molded expansion joint filler, manufactured for 
	expansion joints. Tooled control joints are not to exceed 5'-0" and shall be located to avoid

differential expansion. Joints should not result in small geometries susceptible to cracked corners. Consult Portland cement Association, Cement Mason's Guide Booklet. All sidewalks shall be designed to prevent water from ponding on them; either crowned or sloped and contain ADA approved tactile warnings—refer to Accessibility Guidelines contained in this document.

3. 	Asphaltic Concrete Paving:    Provide materials and installation to comply with requirements of the 
	Florida Department of Transportation and as determined by the civil engineer.  Minimum installation 
	shall consist of 1" plant mixed type S-1 asphaltic concrete surface course over 6" compact base over 
	10" stabilized soil, unless civil engineers determine otherwise.

4. 	Concrete Paving:    Provide Class 'A' concrete with a minimum compressive strength of 3000 psi in 28 
	days.   All products, materials, and execution shall comply with applicable ANSI and ASTM 
	Standards. Provide pre-molded type 2" thick, full depth of concrete, maximum 30'-0" o.c. and at 
	junctions with vertical surfaces. Specify expansion joints and show on the drawings. Control joints 
	shall be saw-cut to squared relief, e.g., 6'0" wide sidewalk, 6'0" space between.  Line up control joints 
	so that new stress points do not occur and cause more cracking of the concrete surface. Provide 
	floated, troweled, and medium broom finished surfaces. The university recommends boring as the 
	standard procedure for crossing streets/roads.   Saw-cut finished surfaces only as a last resort. 
	Concrete walks shall be cut and replaced from joint to joint, doweled to the remaining slab.

5. 	Walks used as vehicular drives shall be a minimum of 6" thick with edges increased to a minimum of 
	2 additional inches thick and 10'-0" wide, steel reinforced.   Secondary sidewalk width should be a 
	minimum of 6 feet, and should match surrounding walk patterns.  Care must be taken to prevent slick 
	finishes, and to avoid the possibility of marking or vandalism while the concrete is curing.  Expansion 
	joints must be properly designed and indicated on contract drawings.   Medium broom finish on all 
	sidewalk Work is required.   Protect concrete from defacement by fencing or providing appropriate 
	personnel to maintain and secure the area until the concrete has properly cured.

6.	The University will not accept defaced concrete.   It is the Contractor‘s responsibility to protect the

surface to prevent vandalism.

7. 	Telecommunications infrastructure- see Appendix A for guidelines for new and relocated duct banks, 
	manholes, conduit runs and other telecommunication components.

24

SECTION 02810 - Irrigation

Part 1 - General

1.1	Scope of Section

This section contains the requirements relating to transmission and distribution systems for irrigation water for landscaping and lawns.

1.2	Overview

All landscaped and sodded areas shall be irrigated with an automatic sprinkler irrigation system, unless approved otherwise as part of water use reduction practices.  The irrigation system shall be designed to minimize water spray on pedestrian walkways and buildings.  All sprinkler lines shall be self-draining and designed to minimize runoff of irrigation water onto roadways, driveways, walks, etc.   Drip irrigation is encouraged where deemed appropriate.   Control systems shall be capable of remote operation and compatible with existing University systems.

1.3	Requirements

A. 	Water Source:   In support of sustainable practices, the University supports reduction of

potable water use for landscape irrigation.   The source of irrigation water should be 
determined in consultation with the University Utilities Department Representative, 
Grounds Department Representative and the Facilities Department Project Manager.

1.  Use of City of Tallahassee supplied potable water for irrigation should be minimized 
	when possible.

2.  All projects should consider other options for irrigation water to include:  existing 
	University irrigation well, captured rainwater, and recycled wastewater.

B.	Metering:  Shall be coordinated with the University Utilities Department.

C.	Backflow Prevention:  Backflow prevention shall be installed on all

25

irrigation systems.   Consideration should be taken to minimize visual impact to the 
Campus.  Provide green covers labeled ―Irrigation‖ and screen with landscape material.

D.	Pressurization:  Pressure on the system should not exceed 75 psi unless

specified otherwise.  Provide an approved pressure reducing valve.

1.4	Materials

A.	Automatic Irrigation Controller - Clock:  Hunter ACC 1200.  Controller

shall be wall mounted, waterproof unit suitable for exterior installation, if required.

1.    The basic controller shall have a minimum of (12) stations capable of 
	being expanded to a maximum capacity of (42) stations.

2.  The controller shall be equipped with an integrated, pre-wired

SmartPort to permit connection of wireless remote controls or other

devices that may be deemed necessary to coordinate new installations with existing.

3.  The controller shall be compatible with a computerized central control 
	via the following Hunter IMMS ACC communication modules:

a.  Hunter ACC-COM-HWR

b.  Hunter RAD3

c.  Hunter ANT3 (RASREM)

B.	Flow Sensor: Hunter Flow-Clik.

C.	Rain Sensor Shut Off:  Hunter Rain-Clik or Hunter Wireless Rain-Clik.

D. 	Electric Valve(s):  All valves shall be professional grade solenoid valves with min. 150

psi rating that provide flow control, dial setting pressure regulation, and have internal and/or external bleed.

E.	Wiring:

a.    Color/Gauge

b.    Strand wire

26

F.	Piping/Fittings:  All piping and fittings shall be schedule 40 PVC installed to allow for

expansion.  Where required, sleeves under walks, etc. shall be schedule 40 PVC and one

size bigger than the pipe it encompasses.

G.	Riser Pipes:  Schedule 40 PVC, painted green in accordance with the height of plant

material.

H.	Valve Boxes:  Provide 10‖ box with locking lid for every irrigation valve.  Lids shall be

marked ―Irrigation Control Valve‖.

a.    High traffic area - concrete box.

b.    Low traffic area - green PVC.

I.	Turf Heads and Sprays:  Professional grade, heavy-duty ABS construction including an

extra thick body and cap.  Spray shall be adjustable from 1-360 degrees by a top

adjustment screw.

J.	Bubblers:  ½‖ pressure compensated adjustable flow up to 2.0 gpm, capable of fine

tuning by top mounted stainless steel screw.

1.5	Execution

A.  Automatic irrigation controller location shall be approved by the Grounds Department prior 
	to installation.

1.  Install irrigation controller per manufacturer‘s instruction manual, including proper 
	grounding procedures.

2.  Clock shall be securely mounted at a height of 5‘ from the bottom of the controller to 
	finish grade.

3.  Clock can be either pedestal or wall mounted as appropriate. Use mounting holes 
	provided.  Do not drill into any controller parts.

4.  Power source shall be hardwired and enclosed in electrical box/conduit in a manner 
	to allow attachment through the controller box knock-outs.  Connection to an open 
	electrical outlet will not be accepted.

5.  Grounding shall be in accordance with ASIC specifications.  Ground rod should be 
	located 8‘ from controller and connected by ground clamp to #6 AWG copper wire. 
	Ground wire shall be enclosed in EMT separate from station and valve wires and 
	installed 12‖ below grade.

B.  Hunter controller modules necessary for wireless communications shall be turned over to the 
	Owner prior to Substantial Completion for Owner installation at a later date.

C.  Where rain sensors are NOT exposed to the elements, install Hunter Wireless 
	27

Rain-Clik rain sensors.

D.  Install piping for both main and lateral lines at a minimum depth of 18‖

below finished grade to top of pipe.   System shall be tested for pressure and leaks in the 
presence of Grounds Department representative prior to backfill.   Backfill material shall be 
free of rocks and other debris.  Piping installation shall include warning tape and tracer wire 
for future use.

E.  Separate zones shall be established for irrigation of trees, planting beds, and

turf.  Wire electric valves to promote sequential testing of the individual zones.  Connection to controller modules shall be one wire per station.  Sprays, rotors, and bubblers shall be on different valves, i.e. do not mix heads on the same station.  All valve wiring shall be bonded and taped every 20 ft.

F.  Provide sleeves for wiring/piping which passes under walks, planters, drives, or other paved 
	surfaces.  Sleeve shall be one size larger than pipe OR larger if necessary to ensure ease of 
	removal and replacement of the irrigation lines without disturbing the roads and/or sidewalks.

G.  Install sprinkler heads to avoid overspray of walks or buildings and to avoid 
	areas of high pedestrian or vehicular traffic.  Give consideration to

maintenance procedures and potential for damage due to head locations.

END OF SECTION

28

SECTION 02900 - Landscaping

Part 1 - General

1.1 Scope of Section

This section contains the requirements relating to lawns, trees, shrubs, flowering plants, and ground covers including design, site preparation, material installation, and removal policies.   Protection of existing landscaping and trees is included in General Requirements.  Irrigation requirements are included in Section 02810 - Irrigation.  Site Lighting is included in Division 16.  Site Furnishings and Hardscape are included in Division 2.

1.2 Overview

Any new construction or renovation of existing construction, which disturbs existing landscaping or significantly alters the building envelope, shall include new landscaping as required to complete or return the project to a level equal to or surpassing the original condition.  The boundaries for the site should be reviewed with the University Project Manager, in order to ensure seamless transitions between adjacent sites, coordinate project overlaps, and to maximize the potential of the open space.

1.3 Requirements

Landscaping design should augment the building design and support the campus aesthetic, while providing for ease of long term maintenance.

The landscaping effort shall include an analysis of the impacts of the proposed construction and its relation to the approved Campus Master Plan, impact of existing adjacent land uses, and identification of any buffering requirements necessary to mitigate incompatible site uses.  The site analysis should include examination of noise, fumes generation, and aesthetic concerns such as adjacency to loading docks, waste storage facilities, utility yards, or other negative impacts.

The designer is expected to encourage positive exterior activities to include:   development of the site hardscape, consideration of anticipated pedestrian and vehicular circulation, promotion of site safety, and encouragement of community connectivity and public transportation access.

1.4 Tree Removal

29

Existing trees are viewed as valuable resources and removal of healthy trees is discouraged.   For 
construction projects, tree removal shall be coordinated with the University Project Manager, in 
consultation with the FSU Grounds Department, during the design phase. Relocation of healthy

specimens may be considered at the discretion of the University.  No removal or relocation should occur without the written approval of the Project Manager.

Tree mitigation may be required.   If so, all mitigation activities shall be supervised by an Arborist certified by the International Society of Arborculture (ISA).

Removal will be considered in the following circumstances upon written recommendation of a Florida 
arborist:

a.  The tree is dead.

b.  The tree presents an immediate safety concern to people, buildings, personal or public 
	property, or circulation routes.

c.  The tree has been infested with an uncontrollable insect infestation, is diseased and threatens 
	other trees, and/or no remedy is feasible.

d.  Removal of trees with a diameter of less than 3‖ will be allowed as part of maintenance, 
	providing the tree is NOT part of a defined research effort or memorial honorarium.

e.  During construction, removal of healthy trees whose diameter is greater than 3‖ will be 
	allowed only when no other option can be shown to be viable.

In support of the University‘s sustainability initiatives, all trees and landscape materials are to be delivered to the FSU Nursery for mulching and later use in University landscape beds.

1.5 Tree Relocation

At the University‘s discretion, trees may be retained and relocated.  Coordinate with Grounds through the 
Project Manager to ensure that the documents adequately reflect all requirements.   Likewise, provide 
instructions  in  the  Construction  Documents  for  relocation  of  other  major  landscaping  and 
groundcoverings.

1.6 Tree Survey and Pre-Construction Preparations

Existing trees to remain should be surveyed and protected from damage during construction.   Identify trees to remain in the new landscaping plan and make provisions to keep damage and stress from occurring to the tree due to construction activity.

a.    Barricades: Before the start of construction, construct a physical protective barrier around 
	existing trees noted to remain.  The protective barrier shall extend as close to the drip line as 
	possible.   Because roots grow beyond the drip line, enclosing as large an area as possible is 
	desirable.

30

b.  Protection from Compaction:    There shall be no additional compaction within the drip line of 
	protected trees.   Storage of construction materials or equipment is not permitted inside the 
	barricade.

c.  Trenches:   Dig trenches by hand or tunnel under the tree if underground utilities must be 
	installed within the drip line.  Prune roots larger than ¾‖ by hand.  Do not rip them out with a 
	trencher or other excavating equipment.   Bridge roots when trenches for new construction 
	would damage them.

d.  Root Pruning:  Prune all roots greater than 2 inches in diameter with a root saw or pruner.  All 
	roots are to be cut cleanly.

e.  Watering:  After root pruning and until substantial completion, all affected tree root zones are 
	to be watered at a rate equivalent to 1 inch of water per week.

f. 	Fertilization:   A slow release (at least on half of the nitrogen shall be an insoluble form 
	fertilizer  to  be  applied  by  broadcast  application  over  the  root  zone  following  the 
	recommended rate.

g.  Limb Pruning:  All limb pruning is to be performed under the direct supervision of a certified 
	Arborist.

Part 2 - Materials

2.1 Quality Assurance

A. 	All planting work shall be done in strict accordance with sound nursery practice and shall

include maintenance and watering of all plant materials installed until acceptance by the University at the time of Substantial Completion.

B. 	Sidewalks adjacent to work areas shall be kept broom clean daily during planting

operation. Plant containers, empty fertilizer bags and containers are to be picked up and 
disposed of daily. Contractor‘s trash shall be removed from the site at the completion of 
work each day.   Any damage to existing sidewalks shall be repaired, or if necessary, 
replaced.

C.	Plant Quality:

1.	Plants shall be in accordance with Florida #1 Grade as specified in ―Grades &

Standards for Nursery Plants‖, Second Edition; published by Florida Department of Agricultural & Consumer Services.

Refer:www.doacs.state.fl.us/pi/plantinsp/publications/g&s_updates.pdf

2. 	Plant material shall be healthy nursery stock, full foliage when in leaf; free from

disease, injury, insects, all weeds, and weed roots. Material should be vigorous enough to ensure survival and healthy growth.

3. 	Container stock should not show evidence of being root bound.

2.2   Materials

31

A.	Plant Selection:    Selection is subject to the design review and approval of the

FSU Grounds Department in coordination with the Facilities Project Manager. 
Diverse and native species will be considered, as well as, the species ability to

promote the educational and research mission of the University.  The following  criteria will be examined:

1.	Existing soil found at the site.

2.	Site hydrology; species irrigation requirements; resistance to drought

3.	Mature height and size of proposed materials.

4.	Disease resistance.

5.	Adjacent site materials.

6.	Shading characteristics of proposed materials.

7.	Appropriateness for climate.

B.	Prohibited Plants:  Non-native, invasive plants identified on any of the following

lists shall not be planted:

1.	IFAS Assessment of Non-Native Plants in Florida’s Natural Areas

2.	Florida Dept. of Agriculture‘s Noxious Weed List

3.	DEP‘s Prohibited Plant List

4.	Exotic Pest Plants Council‘s Invasive Species List Category 1 and 11

C.	New Trees:

1.	Tree Size:  All new trees shall be min. 100 gal. size, unless

approved in advance by the FSU Grounds Department.

2. 	Trees shall be untapped, straight, single leader trees, except for

multiple stem (clump) trees and deciduous trees with heavier than normal top and balanced branching.

3.	Branch systems shall be well-developed.

i.  Material shall be free from disfiguring knots, sunscald injuries, bark

abrasion, evidence of improper pruning, and other objectionable

disfigurements.

D.	All plant material shall be legibly tagged by species and variety with minimum of one

tag per (10) trees/containers.

E. 	All new plant materials shall be inspected by the FSU Grounds Department upon

delivery, and all material not meeting Specification requirements shall be rejected.

32

Contractor shall, at his own expense, replace rejected plant material with material of species and variety that meet Specification requirements.

F. 	All requests for material substitutions must be recommended by the Landscape Architect

of Record and be approved in writing by the University prior to installation.

G. 	Replacements shall be made to same specifications required for original materials

and shall carry the same guarantee from the time they are replaced.

H.	Inspection  and  Analysis  Certificates:	Submit  the  specified  certificates  to  the

University Project Manager for approval by the Grounds Department, prior to or upon

delivery of the materials to the site.

I.	Topsoil:

a.	Topsoil shall be a fertile, friable soil, obtained from well-drained arable

land, and shall be free from nut grass, refuse, roots, heavy clay, clods, noxious weeds or any other material toxic to plant growth.  At least (10) days prior to delivery of topsoil to the site, at no additional cost to the University, the Contractor shall furnish a soil sample from each source along with the analysis and test report for each source.    Written acceptance/rejection of the soil for incorporation into the project will be provided by the University within (7) calendar days.

b. 	To be acceptable the pH factor shall not exceed 8.0 or be lower than 5.5,

soluble salts shall not exceed 1500 PPM, the plasticity index shall be in the range of 3 and 15 inclusive, and it shall contain approximately 11/2%, by dry weight, or organic matter either natural or added.

J.	Weed Fabric:      Do not use weed fabric in landscape beds without the approval of   the

Grounds Department.

K. 	Lawns and Grasses:  Unless specifically approved otherwise, newly grassed areas will be

constructed using sod of a species appropriate to the site location.   Seeding will be 
allowed in large areas with low public visibility only if approved in advance by FSU 
Grounds Department.  Sod shall be sand grown.  No mud grown sod will be accepted.

K. 	Warranties:     All landscape materials shall carry the same (1) year warranty as other

materials supplied by the Construction Manager and shall be subject to replacement at the end of the warranty period, if found to be non-compliant with the contract terms through no fault of the University.

Part 3 - Execution

33

3.1.       Site Conditions

A.        Planting and other site work shall not begin until after the building exterior is

completed    and  remaining construction  activities do  not interfere  with  landscaping activities.

B.       Planting procedures and other site work shall not be performed during wet or muddy 
	conditions.

C.      All existing plant material to remain shall be protected and watered as necessary to 
	ensure survival.

D.      Planting areas should be free of weeds, rocks, and construction debris, adequate 
	soil  preparation completed, and irrigation systems tested and operational prior to

beginning planting of new materials.

3.2	Planting Operations

A.	Backfill Mixture shall consist of equal parts Nitrolized mulch and topsoil.

Backfill shall be mixed thoroughly to ensure no layering of components or clods of soil remain.

B. 	Planting holes shall be as indicated in the contract documents.  All plants are to

be spotted on the site and locations approved by the Landscape Architect in

coordination with the Grounds Department.

C. 	Weed Control:  Prior to placing mulch or pine straw, the area shall be totally free

of weeds, using chemical control as necessary. A pre-emergent herbicide shall be applied by a licensed pest control operator to all planting areas except for areas of native grasses. Treatment shall be according to manufacturer's recommendations and witnessed by the FSU Grounds Department.  Mulch shall be evenly distributed in the designated areas and compacted to a minimum two-inch depth.    A second application of pre-emergent herbicide shall be applied at this time.

3.3	Inspections and Acceptance

34

A.	A written notice or phone call requesting an inspection shall be given the Project Manager

and the Grounds Representative a minimum of 48 hours prior to each anticipated inspection date.

1.  Progress Inspections:  The following inspections will be required.

i.  Tillage and soil preparation of all planting areas.

ii.  Finish grading.

iii.  Inspection and approval of all plant materials upon delivery to the site. The 
	plant material shall be assembled for this inspection.

iv.  Inspection and approval of trees and shrubs at site after being spotted by 
	Contractor.

v.  Inspection of irrigation system before backfilling trenches.

vi.  Inspection for both applications of pre-emergent herbicide before and after 
	placement of decomposed granite.

2.  Final Planting Inspection for Acceptance:

i.  Final inspection of trees and shrubs shall be made at Substantial Completion 
	of the project.

ii.  Upon acceptance at Substantial Completion, the warranty period shall begin 
	and maintenance by the University shall begin.

END OF SECTION

35

EXTERIOR SIGNAGE

All exterior sign types shall be designed in accordance with the Florida Fire Prevention Code, Building Codes and specifications contained in the most recent edition of the Florida State University Signage Style Manual.   Exterior signage requirements should be reviewed with the FSU Project Manager.

STORMWATER DRAINAGE GUIDELINES

1.  Follow these considerations when preparing the design of site storm water drainage and related 
	facilities: Comply with flood plain management criteria.

2.  Determine the impact that the proposed facility has on the current drainage system and plan 
	accordingly.

3.  Building floor elevations shall be set to minimum standards above 100-year flood plain elevation, but 
	in no case lower than two feet above the 100 YFP.

4.  Overland flow capacities from the 100-year storm event available for all flow in excess of capacity of 
	underground and open channel conveyance systems.

5.  No floodwater from the 25-year storm event greater than six (6) inches deep on local roads, parking 
	lots or other non-street vehicular use areas.

6.  No flood waters from the 25-year storm event in one driving lane each direction of collector streets.

7.  No floodwater from the 25-year storm event in two driving lanes each direction of arterial streets.

8.  Where open channel conveyances are to be constructed, storm event in excess of capacity of 
	underground conveyance system, or for full 25-year storm flow if no underground system exists.

9.  The rate of off-site discharge shall not exceed the pre-development rate of discharge.

10. No floodwater from a 5 or 10-year storm event in one driving lane of local roads.

11. No floodwater from a 5 or 10-year storm event in the driving lanes of any other road than a local 
	road.

12. Underground conveyances not overflowing from a 5 or 10-year storm event.

13. Storm Drainage System. Provide catch basin or inlets of precast or cast-in-place concrete?  Grates and 
	frames shall be cast iron or galvanized steel.  Drainage pipe to be concrete, corrugated metal pipe or 
	helicoidal metal pipe (bituminous coated or aluminum).

14. The Construction Manager shall be responsible for obtaining and managing the NPDES Stormwater 
	permit during construction.

BLUE LIGHT SYSTEM

1.  The AE shall include new locations for the University‘s system of emergency blue lights, as 
	appropriate for the project.

2.  The FSU Department of Public Safety shall determine the location of blue lights.

3.  The FSU Department of Environmental Health & Safety, Emergency Management Section shall review emergency blue light placement and potential need to upgrade units with voice loudspeaker capability

4.  For additional information see Florida State University, Telecommunications Infrastructure Standard

- FSU Design Guidelines Appendix ‗A‘.

36

DIVISION 3 - CONCRETE

GENERAL REQUIREMENTS

1.  Require concrete tests as specified in appropriate articles of the SUS Professional Services Guide. 
	For quality control, all material products and execution shall conform to ACI 301 and applicable 
	ANSI/ASTM Standards tests.

2.  Require proper coverage of reinforcement in specifications and during inspection.   Reinforcing bar 
	supports frequently are exposed to the weather on soffits and other surfaces, and corrode.  Use plastic 
	supports.

3.  The Architect/Engineer shall justify the use of admixtures. In general, admixtures are not desired.

4.  Include specifications for cold weather concreting in accordance with ACI 03200.04

5.  Provide proper seals where pipes pass through floors, to be made tight around the piping to prevent 
	passage of vermin, rodents and fire.

6.  Specify proper filler where expansion space is needed.

7.  Provide a straight expansion-joint-filler appearance.

EXTERIOR EXPOSED CONCRETE OR PRE-CAST STONE

1.  No buildings or other structures shall be built using exposed concrete finishes, other than exposed 
	concrete paving and pre-cast architectural concrete or cast stone. Exposed concrete, pre-cast concrete 
	and cast stone using steel reinforcing shall have exaggerated concrete coverage and/or epoxy coating 
	to prevent rusting and spalling.

2.  Do not cut cast stone or other pre-cast concrete pieces that contain steel reinforcement.

3.  Architectural  concrete  specifications  and  inspection  procedures  shall  be  structured  to  ensure 
	compliance with these requirements.

4.  Provide a sample of finished concrete for approval before proceeding.

5.  Employ proper detailing to prevent water and/or copper flashing stains.

6.  Use drip edges and positive drainage to keep water from collecting on horizontal surfaces and 
	discoloring surfaces.

7.  Specify requirements for mock-up construction of areas with windows, flashing, trims, and sealants.

8.  Pre-cast stone and concrete stored on site shall be protected to ensure that identification tags remain in 
	place and damage does not occur causing chipping or cracks.

9.  Employ appropriate measures to lift panels and pieces into place to avoid damage.

10. Patching or other repair of panels must be approved by the Project Manager.

END OF SECTION

37

DIVISION 4 - MASONRY

GENERAL REQUIREMENTS

1. 	Lay concrete masonry units as follows: a) with full mortar coverage on horizontal and vertical face 
	shells. b) Bed webs in mortar in starting course on footings and in all courses of piers, columns and 
	pilasters, and where adjacent to cells and cavities to be filled with grout, c) fill all below grade cells 
	with grout and d) maintain joint widths indicated, with only minor variations to maintain bond 
	alignment, typically 3/8‖ (10 mm) joints.

2. 	Lay solid brick masonry units as follows: a) completely fill bed and head joints, butter ends with 
	sufficient mortar to fill bed and head joints and shove into place, do not furrow bed joints or slush 
	head joints, b) slope beds toward cavity in cavity walls to minimize mortar protrusion into cavity, use 
	a drag stick to keep cavity clear of mortar and trowel mortar protrusion flat against cavity face of 
	brick.

3. 	Lay hollow brick masonry as follows: a) lay vertical cell units with full head joints, unless otherwise 
	indicated, b) provide bed joints with full mortar coverage on face shells and webs, c) lay horizontal 
	cell units with full bed joints, unless otherwise indicated, d) keep drainage channels, if any, free of 
	mortar, e) form head joints with sufficient mortar so excess will be squeezed out as units are placed in 
	position, f) butter both sides of units to be placed, and g) maintain joint widths indicated, except for 
	minor variations required to maintain bond alignment, ¼‖ - 3/8‖ (6-10 mm) unless otherwise noted.

4.	Tool all exposed joints slightly concave when thumbprint hard, using a joint tool larger than joint.

5.	Cut joints flush for masonry walls that are to receive waterproofing or other direct applied finishes

(other than paint), unless otherwise indicated.

6. 	Plasticizers, accelerators, retardants, water repellent agents, or other admixtures are not recommended 
	for mortar unless specifically required and approved by the University Project Manager.

7. 	Tops of all masonry walls, exterior and interior, where applicable, shall be built tightly against the 
	floor construction above for stability, fire and sound protection, except where provision must be made 
	for expansion, requiring alternative means for ensuring stability, etc. Provide masonry and other 
	anchors sizes and spacing in project specifications.

8. 	Composite Masonry mock-up (if required):  Erect a 4 x 4 foot minimum panel size, include specified 
	mortar and accessories. The panel shall show color range and texture of masonry units, bond mortar 
	joints and demonstrate minimum standard for the work.   Completed masonry work in the building 
	shall be equal to that shown in the approved panel.   The panel shall not be removed until masonry 
	work is completed or until removal is authorized.

9. 	Provide concrete block units wherever feasible for interior wall finish.  All units shall comply with all 
	structural codes and shall be properly protected at the job site to insure placing in the wall without 
	excessive moisture content.

10. All walls exposed both sides shall be 6‖ thick, minimum.

11. Provide bullnose on all exposed external concrete block corners that extend to the floor (or to top of 
	base). Rub out all casting irregularities (so as to result in smooth transitions from flat face to rounded 
	corner) before any finish treatment is applied.

12. Provide treated wicks in weep holes.

13. Provide a weep cavity where concrete blocks are veneer faced with brick or precast units.  Face units 
	shall not be installed directly against outer face of interior wythe.  The exterior facing shall be tied to

38

the interior wythe with ties specifically designed for this purpose. A damproof coating shall be provided on the outer face of the interior wythe prior to install the facing..

14. Check split coursing at the head of any type of opening.

15. All brick proposed for historic brickwork, and their range of color, must be approved by the 
	University, and conform to the Secretary of Interiors Standards for color, texture, pattern, bond and 
	size.

16. All face brick shall be standard size with net cross-sectional area not less than 75% of the gross area 
	in the same plane, and must conform to appropriate ASTM Standards

17. All brick shall be laid with modular coursing, three courses to 8", unless otherwise required to match 
	existing coursing or to accentuate an architectural feature or pattern.   ASTM standard shall be 
	complied with for all face brick, Grade SW, Type FBS.  In addition, manufacturer's certification will 
	be required stating that the rating for effervescence is not more than "slightly effervesced" in 
	accordance with ASTM.

18. Glass Unit Masonry. Provide horizontal joint reinforcement, uniform joint treatment interface with 
	adjacent wall systems and compliance with strict structural and code requirements.

19. Masonry Cleaning. Refer to the Southern Brick and Tile Manufacturing Association to for bulletins 
	covering cleaning. (Cleaning should be done sufficiently early for the walls to dry thoroughly; at

least four weeks prior to application of silicone or other recommended waterproofing.  Sandblasting is 
not recommended for bricks, terracotta, or ceramic finished material. Specify that brickwork, 
especially historic brick or stonework must be inspected prior to application of waterproofing.) 
Specify cleaning agents of detergent or solvent. (Acid solution is not recommended and must be

approved by the Project Manager.)

20. Show locations of control joints in construction drawings.

END OF SECTION

39

DIVISION 5 - METALS

EXTERIOR FERROUS METALS

1. 	Structural Metal. All structural steel work shall comply with AISC "Specifications for the Design, 
	Fabrication and Erection of Structural Steel for Buildings" and applicable ASTM Standards.

2. 	All exterior ferrous metals shall be hot-dipped galvanized including all shelf angles and other metal 
	used in cavity walls, whether or not it is exposed to view.

3.	Shop Painting. Has it been specified that all iron and steel items must be shop primed and have

additional coats applied at the job to prevent rusting?

4.	Use galvanized steel angles in all exterior masonry, stone or precast concrete walls, and in all interior

walls where used in conjunction with stone.

5.	Use galvanized steel angles in all interior walls where used in conjunction with stone.

6.	All exterior ferrous metals exposed to view shall be primed and painted with a paint coating designed

for compatibility with the galvanized surface on which it is applied.

7. 	All interior ferrous metal shall be painted with three mils of paint on all.  Use galvanized steel angles 
	in all exterior masonry, stone or precast concrete walls and in all interior walls where used in 
	conjunction with stone.

8. 	All metal components shall conform to applicable ASTM requirements and shall include gratings, 
	castings, supports for ceiling hung equipment and framed partitions, construction inserts and 
	fastening devices, expansion joint inserts and covers, stair nosing and access doors for both ceiling 
	and wall applications, vertical ladder for elevator pit; welded steel ladder (to meet OSHA).  Elevator 
	pit sump gratings; corner guard angles; steel angles, channels and clips; pipe sleeves for mechanical 
	and  electrical  trades; trench  drain  gratings  and frames;  galvanized  steel corner  guards and, 
	miscellaneous structural shapes.

9.	Handrails and Railings. Handrails shall not end in 90 degree angles where there are circulation paths

nor extend more than 3 inches past the circulation areas. All rails:	1-1/2" standard steel pipe. All

posts:	2‖ x 2-1/2‖ standard steel pipe. Comply with all applicable codes.

10. Tree Grates. Tree grates shall be of dimensions as required with concentric patterns having gray iron 
	frame sections and gray iron grate bolted to the frame.

11. Expansion Control. Complete and of compatible materials to produce waterproof expansion joint 
	seals including matching wall, deck and wall, wall and roof and wall intersection systems.

EXTERIOR METAL STUDWALLS

1.  The use of exterior metal stud backup wall assemblies will be considered only on a project by project 
	basis.  The masonry backup wall system is the University’s preferred method of construction.

END OF SECTION

40

DIVISION 6 - WOOD AND PLASTICS

GENERAL REQUIREMENTS

1.  Wood Blocking and Curbing. Provide pressure treated lumber for all lumber in contact with concrete, 
	masonry or steel.  Wolmanizing process is considered best of the treatments for lumber in buildings; 
	Boliden salts are excellent and treatment is equivalent to Wolmanizing if pressure treatment of 
	100/150 psi is used.

2.  If plastic laminate is used, a backing sheet of manufacturer's recommendation must be specified.  This 
	material shall meet flame spread-rating requirements contained in the Florida Fire Prevention and Building Codes for interior finish consistent with 
	the occupancy classification.

3.  All wood shall be back painted.

4.  Minimize the use of wood handrails because of the difficulty of maintaining an acceptable finish. 
	Wood handrails shall return to walls and/or newel-posts.

RESTROOM COUNTERTOPS

1.  Shelves shall be provided in the vicinity of lavatories on which to place books or other personal 
	items.

2.  All lavatory counters are to be solid plastic and have a seamless surface with back splashes at least 
	four inches high and of a light or medium shade smooth material.

END OF SECTION

41

DIVISION 7 - THERMAL AND MOISTURE PROTECTION

GENERAL REQUIREMENTS

1. 	Water-proofing product (sheet butyl, PVC, EPDM, CPE, CSPE, neoprene, hypalon, or composite 
	laminated membrane) shall be designed to function as principal moisture stop in arresting water 
	predominantly in a horizontal application; adhesive bonded, self-adhered, loose laid, or mechanically 
	secured installation.

2. 	Slabs on grade shall be designed and installed so as to prevent damage to membranes during 
	construction.  At special areas and where waterproofing is considered necessary for slab on grade, a 
	double slab system is preferred in order to reduce chances of a punctured membrane.  A product equal 
	to "Bituthane" by W. R. Grace should be considered under the wear slab. For a basement 
	waterproofing condition, a water bar is essential at walls and columns.

3. 	If a Radon Barrier is required, special consideration shall be given to design.

4. 	Provide a through-wall damp-proofing membrane to prevent moisture in the soil from extending up 
	the wall by capillary action.   Material can be as light as 2 oz. copper-backed sisal paper if properly 
	lapped and sealed at joints.

5. 	Basement walls shall be damp-proofed or waterproofed on the soil side.  The type of material to be 
	used depends upon the condition; a brushed-on coat of bituminous paint might be adequate for 
	dampness but sheet membrane waterproofing or "Bentonite" or equal should be considered where 
	hydro static pressure is suspected. Slope grade away from wall and provide drain system, if 
	warranted.

6.	Special consideration shall be given to preventing leakage in shower and drying room areas.

7.	A depressed floor shall be provided for toilet areas where ceramic tile is used to allow space for the

waterproofing pan and slope to drain.

8. 	In waterproofed floor areas, a 24-hour water test required prior to placement of the finish flooring. If 
	leaks occur, another test is required after repairs are made.

9. 	If water repellent materials are applied, provide clear elastomeric water repellent.

10. Design vapor and air barriers so that a continuous seal is formed for the building enclosure.  Seal gaps 
	between adjacent materials forming wall and roof openings.

11. Fire Stopping. Fire stop material shall be used to close openings and continue a fire resistance rating 
	uninterrupted.

12. Gutters and Downspouts. All gutters and downspouts, hangers, straps and shoes shall be completely 
	detailed and/or described.   Gutters and downspouts shall be held 1" from the building wall to allow 
	air to circulate between gutter/downspout and wall surface.   Copper should not be placed in contact 
	with precast stone unless protection is provided.

13. Sealants, Caulking and Seals. Specify the work shall be done by experienced mechanics.  Provide the 
	highest quality of sealants for each individual application.   Evaluate life-cycle costs for sealant 
	products. In addition to caulking for water tightness, caulking shall be specified for finished 
	appearance, i.e., at cracks between the juncture of different materials or of horizontal with vertical 
	surfaces. Caulking is not to be used as permanent construction.   Caulking shall be specified for use 
	only as a supplement to properly designed and detailed joints.   Comply with applicable ASTM 
	requirements.

42

ROOFING

1.  Sheet Metal Flashing and Trim. Provide in accordance with the Architectural Sheet Metal Manual by 
	the Sheet Metal and Air Conditioning Contractors National Association (SMACNA).

2.  Skylight Structures. The University prefers clerestory structures in lieu of skylights. If skylights are 
	used in the building design, the University cannot stress enough the importance of the quality of the 
	skylight and the care of its installation and related moisture protection.   During preparation of the 
	specifications, ensure that performance requirements have been made as stringent as possible.

3.  Scuppers. Provide emergency overflow scuppers in parapet walls to prevent water building up if the 
	roof drains clog.

4.  Gravel Stops. Where gravel stops are used over exterior surfaces, provide high gravel stops, to 
	prevent water from spilling over with resulting stain effect.

EXTERIOR CLOSURE ASSEMBLIES

1.  Don't use exterior wall assemblies that have not been tested for 20 years. EIFS (Exterior Insulated 
	Finish Systems) are not acceptable to the University.

2.  Don't rely on sealants to prevent water infiltration.

3.  Don't use galvanized metal for flashing.

GENERAL ROOFING GUIDELINES

1. 	Roofs shall be maximized, but in no case less than 1/4 inch per horizontal foot. The slope of the 
	roof can be obtained either through the structural design or tapered insulation. The design and 
	workmanship of the finished roof shall be such that no water shall pond on the roof surface more 
	than 24 hours after a rainfall.

2. 	An interior means of gaining access to the roof shall be provided with locking capability.

3. 	The A/E shall specify a minimum of three manufacturers of roofing systems and shall obtain 
	notarized letters from each factory technical representative that the type of roofing system 
	specified will perform in this locality and that all materials delivered to the job site and used by 
	the contractor complies with the specifications. Minimum warranty shall be 20 years unlimited 
	with no dollar limit.

4.	Roof drains shall be unobstructed, properly connected to storm drains and designed and installed

as per the Florida Building Code.

5.	Emergency overflow scuppers shall be constructed below the flashing and not more than one inch

above the roof surface.

6. 	If pre-stressed concrete structural members are used to support flat roofs or roofs with minimum 
	pitch (with or without a light-weight concrete topping poured on the structural members), an 
	expansion joint shall be provided at the ends of each pre-stressed section where the structural 
	members butt together to allow for proper expansion. The roof insulation shall be applied in two 
	layers with no bonding applied between the two layers. Regardless of the thickness required to 
	obtain required pitch or "R" rating, the thickness shall be enough to prevent expansion and 
	contraction of the pre-stressed members. The bottom layer of insulation shall be bonded to the felt 
	layer above. Care shall be taken to avoid coincident placement of joints.

7. 	On all built-up or membrane roofs, roof walkways shall be provided from roof access point(s) to 
	and around all roof installed mechanical or electrical equipment.

43

8.  Don't provide rooftop A/C units or exposed ductwork.

9.  Parapet walls and caps (or coping) shall have through the wall flashing. If limestone caps are used 
	they shall have a lead "T" shaped cap embedded in caulking between each piece of stone cap. 
	Mortar shall not serve this purpose.

10. Warranties from roofing manufacturers shall include coverage for installation as well as 
	materials. In the event of roofing material failure, the roofing manufacturer shall warrant all costs 
	of roofing repairs, including labor. Warranty shall be in effect for as long as the material warranty 
	is in effect.

11. The A/E shall provide full-time inspection service and post-installation moisture testing as 
	required by the above standard practice. The proposed inspector shall be approved by the Project 
	Manager prior to commencing work on the roof.

12. The A/E shall physically verify dimensions where critical to the project design, such as roof 
	areas, room layouts, etc.

13. Roof installations must meet current wind load design standards.

14. Sheet Metal Flashing and Trim. Provide in accordance with the Architectural Sheet Metal Manual 
	by the Sheet Metal and Air Conditioning Contractors National Association (SMACNA).

15. Provide the Solar Reflectance Index for the roof system on the 100% CD Roof Plan.

16. Annual roof scans are executed by the University.   Should the routine scan following roof 
	completion reveal moisture, the contractor shall be responsible for the roof repair and the cost of a 
	repeat scan demonstrating that the roof has been established as ―dry‖.

END OF SECTION

44

DIVISION 8 - DOORS AND WINDOWS

GENERAL DOOR GUIDELINES

1. 	All exterior doors shall be insulated metal doors with adequate weather stripping and threshold 
	utilized to conserve energy. If glass is used, the glass shall be thermal/safety glass, and non-reflective.

2. 	All interior solid core wood doors to be left natural shall be finished with a natural material, which is 
	insoluble and resistant to marring, abrasion and staining.

3. 	Doorframes shall be properly anchored to prevent movement of frame during the opening and closing 
	of the door. Galvanized frames shall be used in exterior applications and interior frames subject to 
	moisture. Frames in masonry shall be fully grouted.

4. 	To prevent the flexing and breaking of the wall along the door frames, a nest of studs shall be 
	provided around each door installation to accommodate the weight of the door and the shock caused 
	by the closing of the door. The number and gauge of studs in the nest must be specified. The finished 
	wall shall extend into the doorframe throat opening a minimum of 1-1/2 inches for wrap-around 
	frames.

5. 	All operable items on exterior doors shall have an integral finish. Not applied, painted, baked-on, etc.

6. 	At least one main entry door shall be accessible from adjacent sidewalks by wheelchair and shall 
	display the proper handicapped signage. Preferably all other entry doors shall have proper signage to 
	direct wheelchair handicapped persons. The current ANSI standards shall apply to raised letter 
	signage for the blind. Provide automatic door opening devices for the handicapped at entrance doors 
	on the accessible path and at main (multi-toilet) restrooms designed for accessibility.

7. 	Exterior doors shall be of "monumental" quality, minimum width of each leaf 3'-0" and minimum 
	height of 7'-0". In renovation projects, a different height may be used, if appropriate, upon approval 
	by the Project Manager.

8. 	Interior doors shall be 3'-0" wide minimum x 7'-0" high each leaf, except that in renovation projects 
	the door height shall match existing. Do not mix door heights in adjacent areas. All doors shall be 
	solid core wood stave. Classroom doors shall have wired glass view panels set in steel framing or 
	stops according to code.

9. 	All doorways shall be numbered. Do not place number on door, but to the open side with raised 
	numbering at a height of five feet. Room numbering schedule shall be reviewed by the Project 
	Manager during Schematic Design and finalized during Design Development.

10. View panels in any fire door shall conform to requirements of Florida Fire Prevention  and Building Codes.

11. Install doorstops on all doors.

12. Hollow Metal Door Frames. All interior frames shall be a minimum of 16 gauge metal.   Exterior 
	frames shall be a minimum of 14 gauge metal. Provide reinforcing of frames for hardware.   A light 
	angle is desirable.   Where two doors swing from the same mullion the metal should be of heavier 
	material and reinforced.  All frames shall be pre-primed

13. If fume hoods or other large equipment occur in a room, provide doors of adequate width to provide 
	clearance for moving the items in or out. If size is questionable, use larger size opening.

14. All corridor doors and doors to closets shall be 1-3/4" solid core to meet requirements of NFPA 80 
	and 101, and able to use standard locksets.   Where cutouts for closers are required, the head rail 
	should be not less than 6 inches.  If hardwood edges are desired, they should be completely specified 
	with the thickness given. Wood doors shall meet the Standards of The National Woodwork 
	Manufacturers Association.

45

15. All doors shall be 7-foot high doors as a standard.

16. Wood door quality shall be clearly specified as well as manufacturer's name noted.  For example, the 
	term "equal to Mengel" is not sufficient.

17. Plastic Faced Wood Doors, Facing and Adhesives. Plastic laminate shall conform to NEMA LD-
	3Adhesives for both exterior and interior shall conform to ANSI/NWMA-I.S.1.

GENERAL HARDWARE GUIDELINES

General

1.  Include a completely itemized hardware schedule in the specification. A cash allowance for finish 
	hardware shall not be used unless otherwise authorized.

2.  The hardware schedule shall include a complete list of items proposed as standard, together with 
	manufacturers' names and with the names of manufacturers whose products are proposed as equals. 
	This schedule must be approved by the University Project Manager at 50% Construction Documents.

3.  All hardware shall be furnished under this section.

4.  Specify one manufacturer as standard and, whenever possible, at least two other manufacturers whose 
	products are proven equal.

5.  The hardware supplier shall furnish to the door manufacturer templates or the actual hardware.

6.  Hardware added to existing buildings will be of the same manufacturer as the existing hardware, 
	unless specified otherwise, and shall include compatibility with the American with Disabilities Act.

7.  Use non-handed door closers whenever possible: Russwin 2800 series, Sargent 1230 series, or LCN 
	equivalent.

8.  When fire exit bolts are required, use horizontal exit bolts for single doors and horizontal exit bolts 
	with removable mullions for double doors. Vertical rod fire exit bolts are not desired unless their use 
	is dictated by specific functional requirements.

9.  All operable items on exterior doors shall have an integral finish -- not applied, painted, baked on, etc.

10. Provide only five-knuckle, stainless steel ball-bearing hinges, with non-removable pins, on exterior 
	doors. Provide heavy-duty ball-bearing butts, with 4 ball bearing for exterior doors and interior doors 
	over 3 feet wide and standard weight butts with 2 ball bearing for interior doors up to 3 feet wide.

11. Provide extra-heavy adjustable pivots at exterior doors that have a high frequency of use.

12. Provide Von Duprin type 99 in a finish compatible with the door.

13. Provide Kawneer Panic Guard, or comparable, at exterior double door aluminum entrances

14. All building entrance/exit doors shall be equipped with exit devices with concealed vertical rods. 
	Surface vertical rods for exit devices are not acceptable. Where exterior doors are required to have 
	a removable center mullion rim type devices may be provided.

15. Provide aluminum or steel removable mullion at all lockable pairs of doors, interior and exterior.

16. Provide surface applied Russwin 2820 series, LCN 4040 series, or comparable closers. Provide 
	Corbin 110 series at dormitories. Locate on room side of doors so not visible from corridors, lobbies, 
	and other public spaces.

17. Use stainless steel at all locations where severe usage is anticipated.

18. Provide weather-stripping at heads and jams and surface applied automatic door bottoms, on machine 
	room doors and other doors where excessive noise is anticipated.

46

19. Avoid thresholds raised above floor levels at doors to trash and receiving rooms and at all doors 
	intended for use by handicapped persons.

Keying

1. 	All door locks, except for MEDECO High Security locks, shall be on the new proprietary University 
	Keying System (BEST Removable Core) as specified by Facilities Operations and Maintenance Key 
	Shop. All keyed locks shall be subject to the Zone Master as assigned to the facility at Florida State 
	University.

2. 	The contractor shall provide extra copies of the approved hardware submittal and current floor plans, 
	showing door numbers, to the University‘s project manager. The project manager will then provide 
	this submittal to the Facilities Operations and Maintenance Key Shop, together with room numbers, 
	the building number(s). In order to allow adequate time for proper ―pinning‖, the project‘s approved 
	hardware submittal must be provided to Facilities Operations and Maintenance Key Shop 120 (one 
	hundred and twenty) days prior to substantial completion for projects containing more than 250 doors, 
	and 90 (ninety) days for projects containing less than 250 doors. The Lock Shop keeps material on 
	hand for small projects having less than 12 doors. Cores can be provided and installed on these jobs 
	with a minimum of two weeks notice. All hardware must be purchased with Best removable core 
	cylinders ―less cores‖. The University will accept no substitutes. Cost of the cores will be borne by 
	the contractor. The contractor must coordinate with the Key Shop, which will procure cores on the 
	contractor‘s behalf. All keys and cores shall be supplied and installed by the FSU Facilities 
	Operations and Maintenance Key Shop, in order to maintain consistency of University master keying 
	systems.

3. 	All keying schemes shall be planned in coordination with Facilities Operations and Maintenance, Key 
	Shop. All Best cores and keys shall be obtained by the University Key Shop. The process shall begin 
	early enough to insure that systems (key plans, keyways, cores) are compatible with Florida State 
	University‘s total Master Keying System, that time phasing is proper, and that the University Key 
	Shop retains control of all keys and cores.

4. 	The Contractor will supply and install temporary construction cores and provide construction 
	personnel and the owner with keys during construction.

5.	The final keying schedule is prepared by, and directly submitted to Best by the Facilities Operations

and Maintenance Key Shop.

6.	In order to maintain consistency, the University will accept no substitutes. Installation and

programming will be done in coordination with the Facilities Operations and Maintenance Key Shop.

7.	All card access will have Best key override, coordinated with Facilities Operations and Maintenance

Key Shop.

47

Guidelines for Campus Card Access and Security

All new construction and major renovation projects shall be designed for the inclusion of FSU Card 
Access systems (a/k/a cCure Card Access).  The plans for placement of card access must be reviewed and 
approved by the FSU Police Department (FSUPD).  The FSU Construction Project Manager will facilitate 
the inclusion of the FSUPD in the early design stages to ensure compliance with security standards. 
Installation of security devices is managed by Information Technology Services network deployment 
technicians.

Perimeter Doors of new buildings must be fully secured through the use of cCure Card Access as follows:

1.  A minimum of two card readers for building access.

2.  Door contact and request to exit at all building perimeter doors.

3.  Removal of key cylinders at all but the two card access doors.

4.  Replacement of key cylinder with Best ―Z key‖ cylinder.

Interior Doors of new buildings may include cCure Card Access, but unless specifically exempted by 
University policy (OP-H-4B-1), interior areas will not have monitoring devices installed (i.e. door 
contacts and requests to exit).   The FSUPD will work with future building occupants to ascertain 
proposed area usage and will make the determination as to whether an interior area qualifies as a 
―mandatory‖ alarm area pursuant to policy.   Previously utilized ―Locknetics‖ devices are no longer 
accepted.

Information Technology Services publishes standards for conduit and electrical infrastructure required for a variety of types of doors (see Door Conduit Standards).   These standards must be followed for all perimeter doors (doors that will have door contacts and requests to exit).   Interior doors that will be monitored require the same infrastructure as perimeter doors.   Interior doors that will not be monitored but which will have card access also require the same infrastructure as perimeter doors except the conduit to the top of the door that would ordinarily be used for the door contact cable.

Other types of security such as closed circuit television (CCTV) camera surveillance equipment and intrusion alarm/burglar alarm systems must also be reviewed and approved by the FSUPD.

INTERIOR DOOR HARDWARE

1.	Use Best mortise lock 35H7J, Russwin ML2255, or Sargent 8237, for classrooms and laboratories.

2.	Use Best mortise lock 35H7E, Russwin ML 2251, or Sargent 8205 for corridor and office doors.

3.	Use Best mortise lock 34H7R, Russwin  ML 2212, or Sargent 8203, for restroom doors. Provide kick

plates, push plates, or pull plates of lexan or stainless steel.

4.	Use Best mortise lock 35H7EW, Russwin ML 2257, or Sargent 8250, for custodial closets.

5.	Hardware trim shall be Satin Chrome, US26D, 626 finish. Trim design: Best 15J, Russwin NSN, or

Sargent WT L, cold forged escutcheon plate.

48

6.	Use astragals on interior double doors for security.

7.	All interior fire doors shall have magnetic door holders actuated by the building fire alarm system,

where appropriate and allowed by code.

EXTERIOR DOOR HARDWARE

1.  Von Duprin shall be specified. (No substitutions).

2.  Single doors - Use a Von Duprin 99 series. Do not use mortise lock.

3.  Double Doors - Use Von Duprin 99 series with removable mullions. Use Russwin 298 foot and head 
	bolts with dust proof strikes, or Sargent equivalent. Do not use mortise locks.

4.  All exit bolts installed on exterior doors should have cylinder dogging devices.

5.  All hinges on exterior doors or doors in security areas should have non-removable pins to prevent the 
	unauthorized removal of the door from the outside.

6.  Exit bolts for narrow stile exterior doors shall be Von Duprin 55 series.

7.  Doors that are of the narrow stile type shall have the same hardware functional requirements as 
	specified for other exit bolts. All double doors shall have a removable rabbeted mullion and each door 
	leaf shall not be less than 36 inches wide.

8.  Provide latch guards at secure exterior doors.

9.  All mullions are to be key locked into the door frame; contractor to provide Best cylinder.

GENERAL DOOR AND HARDWARE GUIDELINES FOR SPECIFIC SPACES

Restrooms

1.  All interior restroom and vestibule doors are to have 10" wide kick and push plates of stainless steel 
	or lexan and are to be non-lockable.

Custodial Closets

1.  Entrance doors shall swing outward where possible.

2.  Each closet lock shall be individually keyed and keyed to the grandmaster system. Classrooms

1.  Classroom doors shall have wired glass view panels set in steel framing or stops according to 
	code.

2.  Classroom doors shall have closers and electric strike hardware for coordination w/the card 
	access system.

HOUSING GUIDELINES FOR DOOR HARDWARE AND CYLINDER BITTING

1.  All student rooms will be keyed differently with grand master and building master.

2.  Bitting number will be provided for all mechanical rooms, electrical rooms, elevator rooms, laundry 
	rooms, and communications rooms.  They shall be keyed to the grand master and building master.

3.  A key shall be established as a janitor and trash room only.

49

4.  Kitchens shall be keyed alike.

5.  In each construction project some doors will have bypass features.

6.  FSU Housing will identify these doors.

7.  All exterior doors shall be keyed alike.

8.  All interior hall doors shall be keyed alike.

9.  FSU Housing will determine the key for offices, storage rooms, and various other restricted areas.

10. If the building‘s rooms are in an apartment layout, each interior student room key will bypass the 
	apartment door.

11.   Furnish four (4) keys with each cylinder.  Bow of key shall be stamped

12. ―Property of FSU Do not Duplicate‖.  Keyway and key number shall be stamped on reverse side.

13.   Furnish fifteen (15) each of the grand master and building master.

14. Furnish one bitting list for owner‘s file.

15.   Visual control number shall be stamped on the plug of each cylinder.

16. FSU Housing will determine mortise lock hardware and exit devices.   Russwin and Von Dupin 
	hardware is preferred.

17. Each exterior door will require 3/4‖ conduit home run to the nearest telephone closet.  The conduit is 
	to include a pull string.  The communication closet will contain a security electronic mode.

18. All exterior doors will be security monitored.  Doors with card readers will be monitored through the 
	card reader, while doors without card readers will be monitored by a door contact.

19. The type of automatic door closers (if needed) and student room door closers will be determined by 
	FSU Housing.

20. The rooms to have door viewers will be determined by FSU Housing.

21. The privacy lock for interior student room bathrooms will be determined by FSU Housing

WINDOW GUIDELINES

1.  Don't locate glass in areas that are inaccessible.

2.  Exterior windows shall be accessible for washing either by manually operable sash, the use of a 
	swinging scaffold or the use of safety gear that snaps onto the window frame. Each window shall be 
	properly equipped with anchors to support safety gear. The architect shall design and supervise the 
	installation of the windows into the building frame, insuring that the windows are adequate and safe.

3.  All windows shall be capable of being opened manually for cleaning and in the event of a shutdown 
	of the HVAC equipment, unless fixed windows are required for control/security reasons. Operable 
	windows shall be provided with positive locking devices. Pivot windows shall not be specified.

4.  Consideration shall be given to the use of double panes (thermopane) with outer shield of solar glass, 
	especially if windows area exceeds 3% of wall area.

5.  Provide guardrails at all full height glass panels in accordance with applicable codes.

6.  Confirm that any hurricane shelter requirements have been considered in the design of windows and 
	selection of window materials.

50

7.  Types of glass and location shall be indicated on the drawings or in the specifications as follows: A 
	"type number" to each type of glass being used on the job. Location of each by the simple note, "glass 
	type 1",   "glass type 2," etc. (Avoid lengthy descriptions of the glass on the drawings.) Each glass

type precisely defined in the specifications.

8.  Use obscure glass in toilet and bathroom windows.

9.  All window glass shall be replaceable from inside the building wherever feasible.

10. Windows shall be glazed in the closed position and left closed for several weeks, particularly awning 
	or projected types.

11. Specify safety glass in all hazardous locations to comply with the Florida Building Code.

12. Selection of window materials shall be assessed for long range, life-cycle cost.

13. Specify aluminum profiles for new construction and renovation, unless specifically authorized to 
	match existing wood windows.

END OF SECTION

51

DIVISION 9 - MATERIALS AND FINISHES

GENERAL MATERIAL AND FINISH GUIDELINES

1.  The selection of materials shall have the benefit of long range, life cycle cost analysis. All selections 
	shall, however, be within budget limitations. It is expected that the A/E will advise the University of 
	all savings opportunities regarding material selections. Solid and hazardous waste disposal costs for 
	excess materials shall be included in the life cycle cost analysis.

2.  The A/E shall coordinate all color and material color selections with the Project Manager. Color 
	schedules will be required for University review with the check set of working drawings. Schedules 
	and samples shall be provided for interior finishes, such as paint, vinyl, baseboards, carpet, tile, 
	bathroom partitions, and the like as well as exterior finishes, such as paint, roof shingles, glazing, and 
	so on. Colors shall be presented in the form of a non-returnable "color-board,‖ which demonstrates all 
	color selections in the form of an overall project color palette.

3.  Samples of all finishes and finishing material shall be submitted to the University for approval no 
	later than the 50% Construction Documents phase. In case of special concrete finishes or stucco work, 
	a sample at least 2'-0" square shall be submitted.

4.  As a minimum, use a latex-based semi-gloss paint on all wall surfaces to be painted to facilitate 
	cleaning. Use water based epoxy paint behind and beneath water coolers, trash receptacles, adjacent 
	to elevations, in vending rooms and in all restrooms. Do not use paint containing lead.

5.  All horizontal, plastic laminate surfaces shall have a matte finish.

6.  Blown-on acoustical ceilings and walls are not acceptable.

7.  For promotion of indoor air quality, low emissive finish systems should be provided.

GENERAL FINISH REQUIREMENTS FOR SPECIFIC SPACES

Restroom Floors

1.  Floors shall be of ceramic, porcelain or quarry tile with dark epoxy grout. They shall have a 
	watertight membrane/sealed so as to prevent seepage.

2.  Floor texture should prevent slips.

Custodial Closet Floors

1.  The floor shall be finished with ceramic or quarry tile and dark grout, or sealed concrete. The walls 
	shall be of ceramic tile or other special waterproof coating material, a minimum of 4 feet high.

CARPET

General Carpeting Design Guidelines

1. 	Refer also to Appendix K - Carpet Guidelines for specific product requirements.

2.  The design professional shall comply with all carpet specification requirements.   No variance from 
	these guidelines shall be approved during the shop drawing process without written approval from the 
	Project Manager.  The University reserves the right to test all carpet materials delivered to the site for 
	compliance with specification requirements.   The Contractor will be liable for replacement should 
	materials fail testing.

3.  Carpet  grain  direction,  seaming,  and  scribing  shall  be  carefully  addressed  in  drawings  and 
	specifications.

52

4.  All carpet, unless otherwise specified, shall run in the same direction. Lay with a minimum number of 
	seams and carpet sections. All carpet is to be smoothly laid with no bubbles, ridges, etc.

5.  Where roll carpet is used, no seams shall occur at doorways and entries perpendicular to doors and 
	entries. Seaming occurring at doorways parallel to doors shall be centered directly under doors. When 
	seams occur at corridors, change of directions shall follow wall line parallel to carpet direction.

6.  Cross-joints, which are necessary due to length of rolls, shall be placed in the cutting, to avoid 
	occurrence at conspicuous locations, near doors, or at pivot points.

7.  Where needed, raw carpet edges at doorways and the like shall be finished with a top quality metal 
	strip or molding.

8.  Do not specify carpet in stairways.

9.  Incorporate patterns to alleviate soiled appearance.

10. Medium dark colors are preferred.

Carpeting And Related Products

The Contractor will be responsible for coordinating material delivery and installation with the sequencing of the work. Carpet shall be installed using an installer, installation materials, i.e., adhesives, edging, etc., and methods approved by the carpet manufacturer.

The Design professional shall be responsible for carpet type and color selection. Based on appropriateness of use, design selections shall be made from the following:

a)  Broadloom Carpet - 12‘ roll goods, woven polypropylene backing.

b)  Hard-backed Carpet - 6‘ roll goods, solid backing impervious to moisture.

c)  Modular Carpet - same as hard backed carpet except supplied as individual solid backed 
	carpet squares. Install with releasable adhesive. Recommended for general use and where 
	additional cleanability, acoustical dampening and durability is desired. Modular carpet is 
	recommended where frequent carpet replacement is anticipated, where access to the 
	substrate is necessary and where replacement of roll goods is impractical due to 
	obstructions in the space.

d)  Solution Dyed Carpet - made with carpet yarn that has color throughout the yarn and 
	therefore has superior color retention and resistance to fading. Solution Dyed Carpet may 
	be supplied as Broadloom, Hard-Backed or Modular.  Recommended for general use and 
	use in areas with high sunlight exposure and/or potential exposure to bleaching agents, 
	such as laboratory zones where chemicals in use may have a bleaching action, and areas 
	near toilets or janitor‘s closets where bleach is used in cleaning.

Use of Carpet

Carpet shall be applied to areas within projects according to the following recommendations:

1.  Very High Traffic Zones - Immediately inside entrance doorways, elevator doors, and other places 
	where traffic is very highly concentrated, use tile, walk-off mats, or similar materials in the immediate 
	vicinity of the doorway, elevator entrance or other high traffic zone. As traffic concentration begins to 
	be more spread out, transition to carpet, using the recommendations below for High Traffic zones.

2.  High Traffic Zones - Modular Carpet is recommended for High Traffic Zones where frequent carpet 
	replacement is likely. Transition to Hard Backed Carpet as traffic becomes less concentrated, and 
	frequent carpet replacement becomes less likely. These zones must be designed carefully and with 
	respect to the challenges of each particular project, but, in general, the designer should consider Hard 
	Backed Carpet in corridors, lobbies, atriums, aisles, walkway areas within open office areas and

53

similar spaces. Give careful consideration to the transition of this thicker carpet to adjoining areas using Broadloom Carpet.

3.  Classrooms - Due to the severe use, likelihood of spills and acoustical considerations, Hard Backed 
	Carpet is recommended for most classrooms. The backing provides this carpet with much better 
	acoustical properties and is much more impervious to moisture penetration.

4.  Areas With High Sunlight Exposure or Exposure to Bleaching Chemicals - Use Solution Dyed 
	Carpet for superior color retention and resistance to fading. Provide this carpet as a Broadloom, Hard 
	Backed or Modular design, depending on the traffic characteristics of the space, as outlined above. 
	Examples of such areas are Atria, spaces located inside large areas of South-facing glass, spaces 
	adjacent to certain laboratories using chemicals with bleaching properties, and carpeted areas adjacent 
	to Janitor‘s Closets and Toilets.

5.  All Other Areas - Other areas, including offices and other spaces, can be carpeted with Broadloom 
	carpet, at the discretion of the designer and University Project Manager. Careful consideration should 
	be given to the use, traffic load, and sunlight exposure of each area in choosing the most effective 
	carpet for that area.

Carpet Cleaning

1.     As job progresses, surplus adhesive squeezed out between joints shall be removed.

2.     Any stains remaining shall be removed by approved methods.

3.  Upon completion of work, all base and edging shall be cleaned, all foreign materials removed by 
	approved methods.

General Carpeting Installation Guidelines

1. 	Use low VOC adhesives unless specifically authorized by the Project Manager.

2.  Installation of carpeting and related items shall be done by a competent contractor normally engaged 
	in this trade with materials and methods complying with the specifications and drawings, and in such 
	a manner as to insure a workmanlike job.

3.  Any existing resilient vinyl cove base shall be cut to obtain a flush edge with the wall.

4.  Sub-Floor Preparation: It is the responsibility of the carpet contractor to remove the existing carpet 
	and pad, where necessary. All surfaces on which the carpeting is installed shall be clean and free of 
	dust, dirt, and debris. Any holes, cracks, depressions, or other imperfections shall be filled and 
	brought to a true plane with non-shrinking grout (similar or equal to "Surco" by W.R. Grace and 
	Company). The A/E shall inspect the surface preparation prior to the installation of the carpet. 
	Moisture tests of substrates are required prior to the installation of carpet and vinyl tile in new 
	structures. A satisfactory reading, conforming to the manufacturer‘s requirements, shall be obtained 
	before installation is permitted.

5.  Damage to the facility or surrounding property incurred by the contractor during any stage of carpet 
	installation shall be repaired and the damaged area restored to its original condition by the contractor 
	at no expense to the University.

6.  Installation of carpet shall not disturb the normal usage of the facility. Therefore, the contractor shall 
	arrange with the University Project Manager a time schedule not concurrent with student, faculty, or 
	staff occupation or use.

7.  Carpet shall not be installed prior to drywall installation.

54

Glue-Down Installation Guidelines

a)  Floors shall be free of all wax, grease, paint, oil or any other substance that would create 
	adherence problems. Cracks, expansion joints, etc. are to be filled with a top quality 
	patching compound and finished smoothly. The carpet contractor shall notify the A/E and 
	the  University  of  any  flooring  conditions  that  would  prevent  the  completion  of 
	satisfactory work.

b)  Floors are to be thoroughly swept and vacuumed by the carpet contractor before applying 
	adhesive.

c)  The mill or factory edge on all roll carpet is to be trimmed far enough in from the carpet 
	edge in order to provide a clean and even seam. Manufacturers‘ recommended cutting 
	methods shall be used.

d)  Cut edges on all roll carpet are to be treated with a seam sealer at the edge of the carpet at 
	the base of the pile and primary backing. On all carpets, excess sealer is to be removed in 
	accordance with the manufacturer's recommendations. To insure an almost 100% contact 
	with the adhesive, the carpet is to be pressed with a roller or push broom per the 
	manufacturer's standard procedures. Note: Carpet with an attached cushion is not to be 
	treated with a floor-covering roller exceeding 30 pounds.

e)  All carpet shall be installed in strict accordance with the approved seaming plan.

f)  Glue down carpet and/or carpet tiles shall not be installed over existing flooring 
	materials.

Carpet Warranty

Contractor Warranty: The Contractor shall give the University a written, notarized warranty guaranteeing carpet installation and related work for a period of one year after the date of substantial completion. The warranty shall commit the Contractor to making all repair and replacement including labor and materials at no cost to the University.

Manufacturer‘s Warranty: The Carpet Manufacturer shall provide the University an unrestricted, full 
replacement, non-prorated, minimum fifteen-year warranty against wear, edge ravel, tuft bind and 
delamination. The Carpet Manufacturer shall coordinate any and all installation and material approvals, 
inspections and certifications required to support the specified warranty with the Contractor and Owner‘s 
Representative.

RESILIENT FLOOR TILE

General Considerations for Resilient Tile

1.  The contractor shall visit the site and familiarize himself with the work to be accomplished. If 
	verification of sub-flooring is required, the contractor shall, upon approval of the Project Manager, 
	remove a portion of the existing flooring material, as required.

2.  The A/E shall submit to the University representative samples and manufacturers‘ literature of 
	materials to be used for approval.

3.  The A/E shall submit no later than the completion of the 50% Construction Documents scheduled 
	information regarding floor tile location, color, material, size, gauge, as well as similar information 
	for base and edging. Specify 12" X 12" X1/8" thick per Federal Spec. FS-312-IV.

4.  Damage to the facility or surrounding property incurred by the contractor during any stage of resilient 
	flooring installation shall be repaired and the damaged area restored to its original condition by the 
	contractor at no expense to the University.

55

5.  Installation of resilient flooring shall not disturb the normal usage of an existing facility. Therefore, 
	the contractor shall arrange, with the University Project Manager, a time not concurrent with student, 
	faculty, or staff occupancy or use.

6.  Immediately upon completion of the tile installation, apply a high quality floor sealer and the 
	minimum number of coats of floor finish recommended by the manufacturer to prevent damage to the 
	floor during construction. Re-coat prior to acceptance of the facility by the owner.

7. 	5% surplus floor tile to be saved for the owner.

8.  Resilient Tile shall not contain asbestos. 
General Resilient Tile Installation Guidelines

1.  Installation of resilient flooring and related items shall be done by a competent contractor normally 
	engaged in this trade with materials and methods complying with the specifications and drawings and 
	in such a manner as to insure a workmanlike job.

2.  Sub-Floor Preparation: All surfaces on which resilient flooring and edging are to be installed shall be 
	cleaned free of grease, dirt, paint, and hardeners. Holes, cracks, and other depressions in the existing 
	floor slabs shall be filled or patched, and brought to a true plane with a non-shrinking grout similar or 
	equal to "Loxon.‖

3.  Floor tile shall be laid with the proper adhesive, meeting Federal specification standards and with 
	close, even joints, to a smooth, even surface, and square with the corridor axis.

4.  Floor tile shall be laid with the grain direction alternating in a checkerboard pattern.

5.  Floor tile at borders on opposite sides of the space shall be equal, and shall be laid, cut, fitted, and 
	scribed to walls, columns, door frames, and the like after laying of the field tile.

6.  Base and molded corners shall be firmly cemented to walls and other vertical surfaces with tight 
	joints. Base throughout its entire length shall have its top and bottom edges in firm contact with the 
	floor and walls. Base shall be scribed accurately to molded corners and to doorframes.

Resilient Tile And Related Products

1.  The University must approve all resilient floor tile and related products. Samples of all resilient floor 
	tile and related products as well as manufacturer's product literature must be submitted to and 
	approved by the University prior to the 100% Construction Document submittal.

2.  Adhesives for flooring and accessories shall be of the types specifically recommended by the resilient 
	material manufacturers, for the installation conditions involved and shall meet Federal specification 
	standards. For the installation of floor tile and edge strips, waterproof adhesive only shall be used.

3.  All resilient tile and resilient base shall be of the same millrun to maintain consistency.

4.  All resilient edging strips shall be vinyl with factory formed feathered edge (similar or equal to 
	Johnsonite Reducer Strips).

Resilient Tile Cleaning

1.  As the job progresses, surplus adhesive squeezed out between the joints shall be removed. Any stains 
	remaining shall be removed by approved methods.

2.  On completion of this work, all tile, base, and edging shall be cleaned as recommended by the tile 
	manufacturer. All foreign matter shall be removed and any chipped or broken tile, base, or edging 
	shall be replaced with sound material.

Resilient Tile Warranty

1.  The contractor shall give the University a written warranty guaranteeing all work performed under 
	56

this contract for a period of one year after the date of completion. In this written guarantee, the 
contractor shall agree to make all repairs or corrections required to maintain the completed work in 
first class condition for the one-year period at no cost to the University. If subcontractors are involved 
in this project, a similar written guarantee shall be furnished by each subcontractor covering his 
portion of the work. Subcontractors' warranties will not relieve the general contractor of any warranty 
responsibility.

STUCCO AND PLASTER

1.  Use galvanized steel metal lath in conjunction with acoustic plaster to eliminate rust stains.

2.  Where conditions require the highest corrosion resistance, specify that lathing accessories such as 
	corner and casing beads be made of zinc alloy.

3.  Provide ample control joints in stucco, particularly in overhangs.   Two No. 60 expansion type 
	casing beads butted together are preferred.

QUARRY TILE

1.  Quarry tile is a desirable material for stairways, corridors, kitchens and for many other areas both 
	interior and exterior because of its enduring quality, ease of maintenance and fire resistance.

2.  Quarry tile treads are preferred for main stairs and should have an integral abrasive of approximately 
	65% aluminum oxide, ceramically bonded at high temperature.

3.  Quarry tile treads shall be replaceable.

4.  Quarry tile specified for exterior slab finishes must have an integral abrasive.

CERAMIC TILE

1.  The current edition of "The Handbook for Ceramic Tile Installation," published by the Tile Council of 
	America, shall be used as a reference guide for selecting design details and specification wording.

2.  Ceramic tile is desirable for floors and walls or wainscots in toilets as well as in some laboratories 
	and utility rooms. Toilet floors shall have dark sealed grout.

3.  Ceramic tile on a masonry wall is insufficient to prevent water from permeating a shower room wall. 
	Specify parging or painting the back of the wall and provide a through-wall flashing near the base as a 
	means of conducting the water back to the shower room floor.

ACOUSTICAL CEILING TILE

1. Use extreme care in choosing the correct acoustic units.   Do not specify exotic patterns, etc.   Ensure that only standard patterns have been specified that will be available for many years in the future.

2. Specify that the Contractor cannot accept discontinued acoustic units, since matching replacements is impossible.

3. Specify that all acoustical ceiling materials shall meet flame-spread rating requirements of prevailing codes for interior finish according to occupancy classification.

4. Specify acoustical ceilings, not only by noise reduction coefficient, but also by tile thickness.

5. Specify mechanical suspension of acoustical ceilings. Adhesive attachment is not permitted. 
	57

6.   Do not specify acoustical tile in dormitories unless specifically authorized and coordinated with the 
Project Manager and Housing Department. Acoustic tile is a poor material to use in dormitories because 
of vandalism.

7.  Where exposed grid systems are specified, a reflected ceiling plan is required on the drawings. 
	Specify construction tolerances regarding plumb, dimensions and locations, particularly where 
	exposed masonry and concrete is used.

8.  Specify that the buildings must be dried by heat or other means prior to installation of acoustical 
	ceilings, to control humidity.

9.  Specify that all suspension systems shall be intermediate duty rated.   Heavy duty systems will be 
	provided if the loading dictates.   All grid systems shall be supported at a minimum of 4ft in each 
	directon in accordance with the provisions of the latest edition of ASTM 635 and 636.

10.   All lay-in light fixtures regardless of weight shall be independently supported from the structure 
	above.

PAINTING

1. 	Require undercoats to have slightly different tints, and to be inspected and approved by the 
	Architect/Engineer prior to application of the next coat.

2. 	Specify the total thickness of paint by "dry mil" or "wet mil" thickness (according to which is 
	recommended by the paint manufacturer), and verify the thickness on the job by use of special low-
	cost gages.

3. 	The university will assist the Architect/Engineer in specifying the quality of paint required, acceptable 
	vendor products and paint specifications for specific types of paint and their application.  Paints with 
	the highest proportion of titanium dioxide should be used for dirt shedding properties.

4. 	Clearly describe substrate preparation requirements.

5. 	Require metal doorframes in masonry walls to be back painted prior to installation.

6. 	Specify paint on steel and iron items on the basis of mil thickness rather than number of coats.  Items 
	exposed to the weather shall have a minimum of six mils total dry film measurement. Interior steel 
	and iron shall have a minimum of four mils dry film measurement.

7. 	Use a clear silicone waterproofing or approved alternative the exterior of all brick buildings including 
	the stone. 3% silicone is considered adequate; for limestone a 5% silicone is desirable.   Products, 
	which have been used and found acceptable, are:  Florida Laboratories Chemclear 30 and Sonneborn-
	Hydrocide S-X.

8. 	Clear silicone waterproofing shall contain a minimum of 3-5% silicone resin solids in a hydrocarbon 
	solvent conforming to formulation and performance standard of Federal Specifications SS-W-OO11O 
	(G.S.A.). Container label shall certify that it meets above requirements.   Where an interior paint is 
	used on masonry or concrete surfaces, no silicone waterproofing is desired.

9. 	Provide  latex based paint for interior applications and an oil based paint for exterior applications and 
	interior metal applications susceptible to contact and wear.  Interior paint shall be no or low VOC to 
	promote indoor air quality.

10. To promote indoor air quality, provide low VOC paints and coatings whenever possible.

END OF SECTION

58

DIVISION 10 - SPECIALTIES

GENERAL ACCESSORY REQUIREMENTS FOR SPECIFIC SPACES

Toilets

1.  Fixtures and partitions shall be wall or ceiling hung to keep floors clear for cleaning. Fastening is to 
	be by means of toggle bolts and through bolts into studding, stringers, or joists to prevent attaching to 
	the wall only.

2.  All items are to be securely installed. In drywall partitions, use solid wood backing.

3.  Solid plastic stall walls are preferable. Santana or Equal, graffiti resistant type.

4.  Provide coat hooks on the inside of each stall door.

5.  Provide soap dispensers - Foam Soap Dispenser, size 1250 milliliters, color gray, uses Luxury Gojo 
	Foaming Hand Soap, Size 1250 Milliliters, Grainger # 3WU72, Manufacturer‘s #: 5150.

6.  Provide toilet tissue dispensers - Toilet Tissue Dispenser, Jumbo Bath Tissue Dispenser, Wall Mount, 
	Material ABS Plastic, Color Translucent Smoke, Capacity 2 rolls 9 inch Jumbo Tissue, Height 12 5/8 
	inches, width 6 inches, depth 7 inches.  Grainger # 4DJU8.  For use with 1PHJ2 or 1PHJ1 bath tissue.

7.  Provide paper towel dispensers - Roll Towel Dispenser, Hands Free Push Paddle, Color Translucent 
	Smoke, Usage Control, Stub Roll Feature, plastic material, height 12 inches, width 11 7/8 inches, 
	depth 9 ¾ inches.  Grainger # 4TE15.    Uses Roll Towels 2U232.

8.  Provide wall mounted semi-recessed stainless steel waste receptacles WITHOUT TOWEL 
	DISPENSER.

9.  Provide stainless steel sanitary napkin receptacles in all female toilet stalls.

10. Soap dispensers must be of the type that use sealed soap, bladder refills (SEE LINE 5).

BUILDING SERVICES WILL NOT SERVICE REFILLABLE DISPENSERS.  They shall be wall-mounted above sinks, one per every two sinks, with an additional dispenser by each sink within independent handicapped accessible stalls.

11. Do not provide ashtrays.

12. Mirrors are to be provided for all restrooms.  Do not place mirrors in open view of the entrance way. 
	Mirrors shall be mounted at a height to be handicapped accessible.

13. Provide water cut-off under each sink with hose adapter.

Custodial Closets

1.  Provide 18'-0" of 12" shelving mounted at 4'-0" AFF.

2.  Provide one built in locker 2'-0" x 4'-0" x 7'-0" with hasp.

3.  Provide wall splash protection.

4.  Provide sink with hose hook up.   The custodial closet sink shall be provided with hot water per 
	OSHA.

59

5.  Refer also to Division 1 - General Planning and Design Requirements. Classrooms

1.  Furnish audio-visual blind systems or other acceptable window coverings, which exclude light in all 
	exterior classrooms.

MARKERBOARDS AND TACKBOARDS

1.  The Architect/Engineer shall schedule the sizes and locations of chalkboards and tack boards with the 
	university project manager during planning meetings.

2.  Provide at least four map hooks per eight feet of length.  Set the tops of marker boards at seven feet 
	above the floor.

3.  Dry-erase marker boards shall be used instead of chalkboards. Marker boards should contain 
	a marker tray and 1-1/2" continuous tack strip at the top.   Mount tray 36‖ AFF to the tray. 
	The dry-erase board should cover as much of the front wall as practical.

SIGNAGE

1.  Refer Appendix B - Signage Specification, for FSU preferred signage requirements.

2.  Room Naming and Numbering - All room numbers will be assigned by the FSU Office of Space 
	Utilization and Analysis. Contact: Lori Pinkerton (850) 644-9660.

3.  Provide marking, signage and other identification for all mechanical equipment and piping.

4.  Provide clear marking in accordance with code for all fire rated wall assemblies.

5.  Provide a sign at each floor level landing in accordance with NFPA 101  and the Florida Building Code.

The sign shall indicate the floor level, the terminus of the top and bottom of the stair enclosure, roof access, and the identification of the stair.   The sign shall also state the floor level of the direction to exit discharge. The sign shall be located approximately 5 ft. (152 cm) above the floor landing in a position that is readily visible when the door is in the open or closed position.

6.  The Architect/Engineer shall include directional signs for direction of the public through corridors to 
	destination together with identification of specific functions of rooms such as, MEN, WOMEN, 
	CUSTODIAL CLOSET, MECHANICAL ROOM, DEPARTMENTAL NAMES, HIGH VOLTAGE, 
	etc.  Observe requirements of the Accessibility Codes.  Particular attention should be given 
	to placement of exit signs to ensure compliance with applicable codes and occupancy limit at 
	designation on signs at specific areas.  Design, placement, and other details will be in accordance with 
	the Fire Marshal's requirements.

CONSTRUCTION SIGN

1.  Before the ground breaking ceremony for a new facility the project construction sign shall be erected 
	by the contractor at a site designated by the University Project Manager, and be constructed according 
	to the requirements shown in Appendix G., It is the contractor's responsibility to insure that all names, 
	project numbers, and personnel are correct and up-to-date. This requirement also includes correct 
	spelling. Mount sign on 2 - 4‖x4‖x12‘ PT wood posts. Removal shall be performed by the contractor 
	at substantial completion.

60

BUILDING PLAQUE

1.  The construction contract shall contain an adequate allowance for the installation by the contractor of 
	a cast metal building plaque.

2.  Location of the plaque in the building shall be as determined by the Project Manager, FSU Facilities 
	Planning and Construction Department.

3.  It shall be the responsibility of the contractor to verify through, the Project Manager, all the 
	information on the Building Plaque, including spelling, project name & number, University officials, 
	etc.

FIRE PROTECTION SPECIALTIES

1.  Unless otherwise required by Code, all fire extinguishers shall be provided by the Contrator, be maximum 5 lb. units, with a 
	3A40BC rating. 10 lb. units may be used in work shops, parking garages, large mechanical rooms, 
	elevator equipment rooms and labs containing large quantities of flammable liquids.  Rooms housing 
	only HVAC systems, small electrical rooms, janitor‘s closets do not require fire extinguishers unless 
	otherwise determined.

Acceptable extinguisher manufacturers:  Amerex, Badger, J. L. Industries, J. W. Moon, Potter-Roeme

2.  CO2 extinguishers - Do not use except with prior approval of the Environmental Health & Safety 
	department.

3.  Fire extinguisher cabinets - Use only UL approved pull open, non-locking keyless cabinets, (unless approved by EH&S for exterior use) with a 
	flat, shelf bottom without interior hanger and sized for a minimum 10 lb ABC extinguisher. All 
	cabinets shall be fully or partially recessed and shall not extend greater than 4 inches from finish wall 
	surface. Do not use break glass or plastic bubble front units. Extinguisher cabinets shall be installed to 
	maintain the integrity and fire rating of the partition system it is installed in.   The words ‗FIRE 
	EXTINQUISHER‘ shall be clearly visible on the exterior face of the cabinet.  Additional signage will 
	be provided to guide occupants to a fire extinguishers location if hidden by columns or other building 
	components.

4.	Buildings and spaces without fire extinguisher cabinets shall have all extinguishers surface mounted in locations in accordance with the requirements of NFPA 10.

5.  Use Halatron or FE2000 fire extinguishing agents in computer rooms and laboratories where sensitive 
	equipment exists. 2AC rated water mist extinguishing systems may be used in computer server

rooms or laboratories with department approval.

6.  Use K - Type extinguishers in commercial kitchens meeting the requirements of NFPA 10.

LOUVERS

1.  All wall louvers shall be extruded aluminum, storm proof, and include bird screens.

2.  All louver perimeters shall be sealed to provide full perimeter integrity.

3.  Meet Florida Product Approval Requirements for exterior walls.

WALL AND CORNER GUARDS

4.  High impact vinyl and stainless steel may be used with approval of the University Project Manager. 
	Provide 3/16" or a heavier gauge PVC to prevent warping.

5.  Light gauge aluminum is not satisfactory.

END OF SECTION

61

DIVISION 11 - EQUIPMENT

CENTRAL VACUUM SYSTEMS

1.  Where project budget permits, install central vacuum systems in all new facilities, which are to be 
	carpeted.

TRASH HANDLING EQUIPMENT

1.  Trash removal should be discussed with the Project Manager and methods for trash removal will be 
	considered on an individual basis in consultation with the User group and the FSU Grounds 
	Department.

2.  Pay particular attention to fire prevention problems associated with trash removal and storage.

3.  Establish on site recycling areas accessible to staff members assigned to the collection and pickup of 
	recyclable materials. (I.E. immediately off loading docks or accessible by paved sloping walkways,

not stairs.)  Recycling containers shall be planned and located inside all new buildings at a minimum of (1) area per floor.

4.  Dumpster locations should be designed with consideration for ease of access and pedestrian safety. 
	Dumpsters should be enclosed in fencing or screened by landscaping to provide aesthetic relief.

LOADING DOCK EQUIPMENT

1.  All loading docks shall be equipped with leveling platforms and be covered to accommodate 
	deliveries in inclement weather.

END OF SECTION

62

DIVISION 12 - FURNISHINGS

GENERAL GUIDELINES

1.	The University prefers standard items to reduce costs and maintenance or replacement problems, in

preference to special items.

2. 	Recessed trash receptacles shall be located outside each classroom door, each elevator door, and each 
	building entry and in all hallways and lobbies. Recessed, wall mounted trash receptacles shall be 
	located outside each designated classroom door, each elevator door, and each building entry. 
	Receptacles shall have hinged doors or be removable. Cigarette urns shall not be provided except near 
	building entrances, where sand urns shall be located.

3.	Building directories shall be provided in all main lobbies.

4.	All shelving shall be adjustable except when a specific installation is impractical.

5.	Bulletin boards and display cases shall be provided as designated by the user.

6.	For classroom areas, provide good quality marker boards in long sheets with a tack railing provided

on top of the board.

7. 	Entrance floor mats should promote indoor environmental quality and shall be recessed flush with 
	finished floor and be provided inside and outside of all building entrances. Where possible, recessed 
	and replaceable walk off mats shall have a 12-foot run length inside of all entrance doors. Exterior 
	mats shall be a minimum of 4x6 for a single door, and 6x8 for a double door. Exterior mats shall be of 
	the type to scrape and remove heavy dirt and soil. Interior mats shall be absorbent and be constructed 
	so as to trap sand and finer particles. For projects seeking LEED certification, comply with Indoor 
	Environmental Quality Requirements.

8. 	Stored pressure dry chemical, refillable, multipurpose ABC type fire extinguisher shall be provided in 
	each hose rack cabinet and at other locations as required by the NFPA.

9. 	In rooms designed for frequently moved furniture or equipment provide a chair rail or guard around 
	room perimeter to protect wall finishes. Coordinate design and location with the University Project 
	Manager.

10. Provide an interior signage system meeting ADA requirements.

11. Provide exterior signage meeting ADA requirements as appropriate.

WINDOW TREATMENT

1.  All exterior classrooms with exterior openings are to be furnished with audiovisual blind systems, 
	which exclude light.

FIXED SEATING SYSTEMS

1.  The A/E shall request and receive shop drawings for the installation of fixed seating in auditoriums, 
	theaters and lecture halls. He shall request that a sample installation be done for testing and the 
	Project Manager and University representatives shall approve the test installation before approving 
	shop drawings for the complete installation.

2.  Provide for ADA compliance in all fixed seating solutions. Any exceptions must be reviewed with the 
	Project Manager.  ADA waiver requests shall be the responsibility of the design professional.

63

LABORATORY CASEWORK

1.  The A/E is required to obtain sign-off from University personnel for the selection of acceptable 
	laboratory casework construction, materials and manufacturers.

2.  Select working surfaces for the intended use. Plastic Laminate tops are satisfactory for many labs but 
	epoxy countertops must be specified where top is exposed to heavy usage, strong chemicals, heat, etc.

3.  In order to obtain full information directly from lab users, the University Project Manager shall 
	arrange conferences with the appropriate University personnel and the A/E to discuss laboratory 
	design and specialty construction such as environmental rooms, diagnostic labs, coolers, sound proof 
	rooms, etc.

END OF SECTION

64

DIVISION 14 - ELEVATORS CHAIR LIFTS AND DUMBWAITERS

IT IS RECOMMENDED THAT AN ELEVATOR CONSULTANT BE RETAINED TO ASSIST WITH ALL ELEVATOR, DUMBWAITER AND CHAIRLIFT 
SPECIFICATIONS AND DESIGNS.

1.  HANDICAP REQUIREMENTS:

1. 	Elevators and Chairlifts shall be handicapped barrier free in accordance

with design standards of the National Elevator Industry, Inc. ANSI A-
117.1 and ADA Standards.

2. 	The height of the center of the operating buttons shall comply with

all codes enforced at the time of installation of the equipment.

2.	ELEVATOR MANUFACTURER AND CONTRACTOR REQUIREMENTS AND

QUALIFICATIONS:

1. 	An approved manufacturer regularly engaged in manufacturing elevator

equipment of the type required for this project

1. 	The manufacturer or authorized agent of an elevator equipment

manufacturer with not less than ten (10) years of satisfactory experience installing and servicing elevator equipment equal in character and performance to the 
project elevator. Any welding on the site must be performed by personnel who 
have successfully passed an American Welding Society authorized test and whose welding work has been judged by a natural person who is fully authorized to do so by the American Welding Society. The authorized person who evaluates the 
welding must sign the certificate signifying applicant has passed required 
tests. No substitutions will be permitted.

2. 	The Installation Contractor must submit catalogs and show evidence that

all required parts are kept in inventory within ten (10) miles of the elevator 
installation. The Installation Contractor must certify that he/she has a Service 
Office with full time employees within ten (10) miles of the project site.

3.  The Elevator Contractor must pay the expenses of a ―QEI‖ Certified

Elevator Inspector not employed by the installing Contractor to witness 
all testing of the equipment again immediately prior to expiration of the 
twelve (12) months warranty period. A Copy of the testing report must be 
turned over to the Owner and to the Elevator Contract Administrator for 
the University.

4.  The cost of all elevator inspections and certificates are to be paid for by

65

the Contractor.

III.	ELEVATOR MAINTENANCE:

1.	Elevator maintenance and warranty on new and/or up-graded elevators

shall be for a period of 12 months after acceptance. The Certified

Mechanic must spend a minimum of two (2) hours per month per traction, one (1) hour per month per hydraulic, one (1) hour per month per 
dumbwaiter and/or one (1) hour per month per chairlift regularly and 
systematically cleaning, examining, adjusting lubricating per 
Manufactures Recommendations.

The approved elevator maintenance Technicians must be certified with a 
―Certificate Of Competency‖ from the State of Florida. The Contractor 
shall be responsible for providing additional maintenance, repairs, service, 
call-backs and other work on a 24 hour, 7 days per week basis as part of 
the installation or modernization contract Response time for any problem 
calls must be with in one (1) hour after notification of the problem.

1.	ELEVATOR PIT AND HOISTWAYS:

1.	The elevator pit area, which includes the floor and walls up to the lowest

landing threshold area must be water sealed and painted with two (2) coats of high

gloss acrylic latex floor enamel.

9.	Pit ladders are to be installed according to all codes enforced at time of

installation. Location of ladder is to be determined by the Elevator Contractor and

Designing Firm.

10. Sump holes to be installed in Pit, covered by grate. If Sump is to be used, installation of 
	Sump Pump must be installed according to all codes enforced at time of installation.

11. Conduit and Lighting Fixtures in Pit are to be installed for WET

conditions. All codes governing this type of lighting system at the time of installation must be followed.

12. All voids, holes, slots, etc., in the hoistway shall be grouted or pointed up

to obtain fire rating. All nails, snap-ties, form straps and wood shall be removed from hoistway.

13. Where needed, grating shall be provided in shafts to permit safe 
	lubrication of sheaves and equipment.

2.  ELEVATOR MECHANICAL ROOM:

66

1.	The elevator machine room shall be no larger than necessary to house

and repair machinery. The elevator machine room walls and ceiling must be primed and completely painted with two (2) coats of semi-gloss acrylic latex paint. The machine room floors shall be smooth and level. The elevator machine room floors must be painted with two (2) coats of highest quality oil based light gray color gloss floor and deck

enamel.

2. 	The elevator machine room shall not to be used for storage of any kind. No 
	foreign piping, ductwork or conduit shall pass through hoistway and/or machine 
	room. With the use of Microprocessor based elevator control system, the Elevator 
	Mechanical Room must be environmentally controlled. All nails, snap-ties, form 
	straps and wood shall be removed

from machine room walls and ceiling.

3. 	All elevator machine room doors must be self-closing, self-locking,

requiring a key to open. Door must also have a sign stating ―Danger-
Elevator Equipment‖. Machine Room Doors shall be not less than one 
and one-half  hour fire rating B label, not less than 3‘ 4“ in width 
and not less than 6‘-8” in height. Doors shall be provided with a spring type lock arranged for opening from the inside without a key. A key is required to open the door from the outside.

4. 	Elevator machinery rooms must be well lighted in order to provide a safe

environment for the elevator technicians to work. Lighting must be at least 
19 foot candles, measured at the floor, in all portions of the room. Lighting 
must have guards to protect lamps. Light switch shall be located on the 
lock-jamb side of the access door. Elevator machine rooms shall 
have a head room of not less than 7‘0”, (Head room is determined by 
measuring from the floor to overhead items such as wire duct, beams, 
lights, etc.

5.	Stairways for access to elevator machine rooms shall conform to the requirements of the Florida Building Code.

6.  Access to elevator mechanical rooms across roof shall have steps or ramps 
	with metal railing built over pipes or other obstructions.

7.  All Electrical disconnects, fusing and receptacles shall be installed 
	following all Codes enforced at time of installation.

8.  All hoist way vents shall be installed following all Codes enforced at time 
	of installation.

9. 	Elevator machine rooms shall not be located adjacent to classrooms and

other noise sensitive spaces without thorough consideration to noise transmission to these spaces.

VI.   PAINTING OF EQUIPMENT:

1. 	Elevator equipment must be completely painted in the field, except

for the stainless steel and for the polished machined surfaces of the hydraulic buffers, guide rails and/or hydraulic plungers.

1. 	ELEVATOR   SERIAL   NUMBER   SPECIFIC   OPERATION,   ADJUSTMENT   & 
	MAINTENANCE DATA; TOOLS OR COMPUTER DEVICES, FOR EACH ELEVATOR 
	(OR  FOR  EACH  MULTI-CAR  GROUP  ELEVATOR  SYSTEM)  ELEVATOR 
	ELECTRICAL  CONTROLLER  AND  DOOR  OPERATOR  CONTROL,  IS  TO  BE 
	PROVIDED TO OWNER:

Elevator Contractor shall provide four (4) copies of typewritten or professionally printed,  elevator  serial  number  specific  installation,  adjustment  and troubleshooting instructions, to be used in maintaining and repairing all new, upgraded or renovated elevators or group elevator systems.

Elevator Contractor shall provide four (4) copies of the elevator serial number 
specific, as built, electrical wiring diagrams, designed with point to point wiring 
or circuit connections.   Further, furnish a complete set black on white drawings, 
printed on high rag content paper for long life, to be used for reproduction of 
wiring diagrams, if needed in the future.     Additionally, provide one (1) complete 
set of the same high quality wiring diagrams, laminated with heavy gauge clear 
plastic, and designed to be hung on sturdy wall bracket(s) in the elevator machine 
room(s).  Drawings shall be designed to be easily removed from the rack for use 
by the elevator technicians.

68

Elevator Contractor shall provide four (4) copies of all elevator serial number specific computer or handheld adjustment device passwords, legends, reference codes, key words, operational descriptions and related information so that a competent  elevator  technician  can  access  the  elevator  electrical  controller system(s), make adjustments to the equipment settings, determine the malfunction codes, troubleshoot the electrical system or verify correct operation of the elevator electrical controller or door operator equipment.

Elevator Contractor shall provide four (4) copies of an elevator serial number 
specific replacement parts list for each elevator or group of elevators, located in a 
new building, or that which is renovated or up-graded in an existing building. 
Elevator Contractor shall have the right to furnish either ―on board‖ mounted 
computers or hand held diagnostic devices, or similar portable computer or hand 
held devices that can be disconnected from the elevator electrical controller and 
door operator controller systems.   Either design is acceptable so long as the 
required  maintenance  and  adjustment  information,  diagnostic  functions, 
equipment operation, equipment performance and troubleshooting activities can 
be performed without unnecessary delays, and the same performance results can 
be anticipated.   Regardless of the type of computer or diagnostic equipment 
provided under the contract, the Elevator Contractor must provide the Owner with 
one (1) complete set of computer or handheld technical equipment devices that 
will operate each and every elevator covered by the new elevator or elevator up-
grade contract.

Provide a complete set of current, as built and installed, microprocessor software for each and every elevator covered by the contract.

The Elevator Contractor must provide a notarized letter with his bid that states 
that, if he receives the contract to perform the elevator work, the Elevator 
Contractor  shall  provide  all  of  the  required  installation  and  adjustment 
information, computer devices or service tools, data, instructions, diagrams, parts 
lists and related information at the time the project is completed. 
All required information, data, diagrams, instructions and related materials shall 
be provided in heavy duty, oversize type, three (3) ring binders, properly

identified with the project name, locations, elevator serial numbers, building elevator numbers and related information.

2.  REPLACEMENT PARTS:

9.  All of the major parts utilized in new or up-graded elevators must be manufactured in North 
	America, and the elevator manufacturer must have a documented quality assurance program.

10. Only new parts or components shall be accepted.  The installer shall not use rebuilt, used or 
	reconditioned equipment or parts on any new elevators or up-graded elevators.   The only 
	used equipment allowed are existing components that are specified to be reused during an 
	elevator up-grade contract.  None of the parts or equipment removed from the project can be 
	used elsewhere on the Florida State University Campus.

69

11. The Elevator Contractor, and Elevator Manufacturer, if not the same company, must provide 
	a notarized letter at the time the elevator work project is bid stating that all necessary 
	replacement parts, supplies and related equipment, necessary to maintain, repair and service 
	the elevator equipment will be promptly sold, without delays, directly to the Owner, or to the 
	Elevator Contractor who maintains the elevator equipment on behalf of the Owner without 
	the necessity of the replacement parts being initially purchased by the Owner.   The letter 
	must be signed by an executive officer of the Elevator Contractor.

3.  FASTENERS:

1.	All exposed screw is to be of the vandal (tamper-proof) type.

Include countersunk, vandal resistant, 316 stainless steel screws for

cover plates.

2.	Drive pins to attach any surface mounted Braille plates.

4.  THRESHOLDS/SILLS:

1.	In Cab - Nickel Silver.

2.	Landings/Floors - Floors with heavy traffic Nickel Silver

XI	DOOR OPERATORS:

1.	Elevator Door Operators must be highest quality, heavy duty type, with

―closed-loop,‖ type microprocessor digital control system. Door operator

must have digital encoder.

a.	Include the following features in door operator control system:

Door position monitoring

Door velocity monitoring

Door motor current monitoring

Door closing pressure monitoring. Doors must reopen when door pressure setting is reached in closing direction.

XII.  LANDING STATIONS:

1. 	Push - button stations located at each landing that includes mirror

finished, vandal resistant, stainless steel buttons with flush jewels

in the center that indicates that the call has been registered. The call

registered jewels shall light up brilliant red with the use of ultra-bright

light emitting diodes. The cover plate shall be made of no. 4 satin finished no. 316 stainless steel, minimum of 1/8 inch thickness, approximately 7 inches wide and shall be of an overall size that will contain the

70

following:

a. 	Either single (terminal floors) or double buttons (intermediate

floors) of the appropriate diameter to meet code for handicapped.

b. 	Engraving and red epoxy filling of a sign to indicate ― IN FIRE

EMERGENCY, DO NOT USE ELEVATOR - USE EXIT STAIRS.” Use ½ inch high letters. Also, provide a flame 
Pictograph symbol of the appropriate size, utilizing a durable plastic insert mounted from the rear into a laser cut hole, or by engraving and filling the area with the required colors of epoxy material for long life service.

XIII.	FIREMAN‘S PHONE AND RECALL:

1.	Fireman‘s phone jack neatly incorporated. Do not provide an

exposed nut on the front of the station. Shielded pair of wire to be

run from each jack to junction box at a location outlined by the Owner.

9. 	Verify location of Fireman‘s recall switch and instructions with Fire

Department and Architect. Instructions should be engraved into plate and 
filled with red epoxy. Provide for Phase I and Phase II operation. Include 
suitable fireman‘s insignia type jewel in station. The fireman‘s 
jewel the designated floor station will flash in the event the smoke 
detector activation was in the machine room or hoist way. Switch 
shall be keyed to match the fire service key currently being used 
on the FSU Campus, key number G-1617X. If local codes call for a 
different type of  Fireman‘s Service Key, the G-1617X key must not be 
used. Engrave instructions in designated landing push button station and in 
cab front return panel.

XIV.	HYDRAULIC ELEVATORS:

NOTE: ALL HYDRAULIC ELEVATORS MUST BE INSTALLED

ACCORDING TO ALL CODES AT THE TIME OF INSTALLATION.

1.	A Hydraulic Elevator can only be used when total travel is less

than fifty (50) feet.

2.	The Motor Starter for new or up-graded hydraulic elevators must be

soft start type, adjusted to a maximum of three (3) times the full

load running current.

3.	Elevators not on Emergency Generator System must be place on a

Battery Lowering System.

71

4.	Provide highly accurate electronic load weighting device, overload alarm

and signal light. Alarm and signal light shall function if load exceeds

design capacity. Elevator shall not function if overloaded conditions exist.

5.	All door frames, headers, etc., shall be grouted solid to maintain fire

rating.

6.	The hydraulic cylinder assembly shall include the following:

a.	The hydraulic jack assembly (cylinder) shall be a complete

new assembly of the highest quality available, and

manufactured in strict accordance with ASME A17.1-1996, 
Safety Code for Elevators and Escalators, including the 
latest published addenda as of the date of the written 
specifications. The total length of the cylinder must include 
the required over - travel at top and bottom landings

b. 	Multiple sections on the plunger and cylinder, if necessary,

to permit ingress into the building and Hoistway without damage to the building or the equipment.

c. 	The hydraulic cylinder must have external, threaded type couplings for

multi-section cylinders. There shall be no materials at the coupling(s) that reduce the interior clearance of the hydraulic cylinder.

d. 	The jack packing seal around the plunger must be of the

molded type that does not require adjustment. The packing gland must be designed to accept the molded packing or seal that is clamped in place without the use of unusually high pressure on the attachment bolts.

e. 	The top of the cylinder shall have a ring for collecting the

oil that seeps past the jack packing and/or wiper ring.

Provide a new drip tube from the top of the cylinder to new five (5) gallon collection container that has a small entry hole for the drip line. Leakage of more than one 1/2 gallon per month will not be accepted.

f. 	The jack assembly shall be supported on a pair of new steel

channels of adequate strength that are approximately as

long as the distance between the elevator guide rails.

Reinforce mounting brackets shall support the weight of the 
fully loaded elevator and cylinder on the pit channels. The 
pit channels must be at least 6‖ in height, and weighing at least

16.3 pounds per foot. The pit channels shall be capable of

72

supporting the vertical reaction on the hydraulic cylinder and the full loaded car without deflection.

The pit channels must receive a rust inhibitive primer and two (2) finish coats of paint before installation.

7. 	Additional Protection Against Electrolysis: The entire hydraulic

jack assembly shall be completely electrically isolated from the entire building, elevator car/platform, pumping unit, pit mounting channels and all other components of the elevator by using the following insulating techniques:

a. 	The jack plunger shall be isolated from the elevator car/platform assembly

through the use of specifically designed rubber isolated platen plate that will no allow metal to metal contact and absorb pulsations from the hydraulic pump. The minimum thickness of the

rubber under compression from a fully loaded car shall be at least 3/4 inch.

b. 	The hydraulic cylinder assembly must be isolated from the jack support

channels and the pit floor. The material to be used between the cylinder 
mounting brackets and the top of the support channels is Micarta or any 
high quality high pressure plastic laminate material of at least 3/8 ― 
thickness. The backs of the channels must be isolated from the top of the 
cylinder with a double wrapping of high quality rubber sheeting material, 
which is wrapped around the top area of the cylinder (behind the pit 
support channels) and secured with an oil resistant cement. The pit support 
channels must not make metal-to-metal contact with the cylinder. The 
bolts that attach the support brackets to the support channels must be 
positively insulated with high strength rubber. Micarta or schedule 40 
PVC insulating material around the bolts, washers and nuts to prevent 
metal to metal contact between the cylinder and the cylinder support 
channels.

c. 	The oil pressure supply line must contain at least two

(2) rubber isolated sound and vibration isolation couplings the

effectively isolate the pumping unit from the cylinder. The blow-
out proof isolation couplings must be installed in the machine 
room as required by ASME A17.1. The oil pressure supply line, 
from the point of the isolation couplings, must be 
completely isolated from the building structure, pit 
floor and any other material in a manner that is 
effectively isolated to prevent a grounding effect. The 
use of high quality rubber materials at least 3/8‖ thick 
when fully compressed will be acceptable as an

73

isolation material for pipe supports or hangers.

Electrical isolation couplings without sound

and vibration-absorbing properties are not acceptable.

9. The oil pressure supply line shall be insulated from the building structure, walls, supports and 
	all other contact points. Where the piping penetrates a wall, the piping shall be insulated with 
	rubber materials at least 3/8‖ thick when compression.

e. 	The complete isolation of the jack assembly must be

checked during installation, and after the installation

work has been completed to verify that there is no

electrical path to ground. Elevator Contractor must use

a megger and high quality ohmmeter to verify that his

work complies with these work specifications, and the

effectiveness of the isolation must be demonstrated in

the presences of representatives of Florida State University.

The Elevator Contractor will be required to remove or correct any 
work that does not fully comply with the isolation requirements.

8. 	Hydraulic Oil Line: The oil line shall include the following:

1. 	The oil line shall be schedule 80 thickness, with threaded forged

steel fittings at all locations where the oil line must change directions or be coupled. Victaulic or similar brand clamp type fittings are not permitted except that one (1) Victaulic fitting may be utilized where the oil line 
connects to the hydraulic control

valve at the pumping unit so long as it is correctly installed and not 
used to correct for alignment deficiencies in the oil line. All 
threaded fittings must be sealed with Expando brand thread sealer. 
Install a high quality ground joint union near the hydraulic 
cylinder. Flexible hoses shall not be used under pressure in this 
installation.

b. 	Install the pipe rupture valve adjacent to the hydraulic

cylinders. The valve must be adjusted to properly to stop the decent of the elevator car in the event of pipe or valve rupture; however, the passengers should not be burdened by unnecessary closure of the valve when no 
emergency exists.

c. 	Two (2) oil shut-off valves must be installed in the oil

line. One (1) shut-off valve shall be installed adjacent to the pumping unit, and is to be provided for purpose of being used when the relief pressure is tested on an annual basis.

74

One (1) line shut-off valve is to be installed near the hydraulic jack

cylinder and is to be used only when the packing is replaced in the jack.

Elevator Contractor shall attach a laminated plastic tag on the 
valve handle stating that the valve is to be used for packing 
replacement purposes only. The lettering on the tag shall be with 
3/8 inch high letters stating the following: ―Caution!! This valve is 
to be used when serving the cylinder only. Do not use for hydraulic 
system pressure tests.‖ tag lettering must be a contrasting color to the 
surface.

The bursting strength of both valves shall comply with the

requirements of ASME A17.1, Section 1302, Safety Code for Elevators.

d. 	Perform all the necessary cutting as may be required to run or install the

oil supply line from the machine room to the hoist way, including the

work necessary to completely isolate the oil line from the building or other building systems. Isolation of the oil supply line must be neatly installed, and be rubber at least 3/8 inch thick while under compression.

1. 	Hydraulic Muffler Device: The Oil line must be equipped with an

effective muffler device that removes the hydraulic pump

pulsations and noise before being transmitted to the hydraulic cylinder through the oil supply line. The muffler must have rubber absorbing 
materials that can be replaced on a regularly scheduled 
basis. The muffler device shall be held together with high strength bolts and designed to be serviceable without removal from the oil supply line. Connections must be threaded. Include a metal tag on the muffler to 
indicate the required service by replacing the rubber pads every two (2) years. Locate muffler device in the elevator machine room area in a 
manner that will not inhibit the service work.

7.	Hydraulic Oil:

a.	The hydraulic fluid for all new or up-graded hydraulic	elevators must

be manufactured by Hydro-Safe Oil	Division, grade VG-32,

biodegradable type vegetable oil.

Install a large data plate on the power unit identifying the oil that

has been installed in the system.

8.	Pumping Unit:

a.	When the motor of the pumping unit is 40 horsepower or less, the

pumping unit shall be of the type with the pump and electrical

75

motor submerged in the oil supply in reservoir. Oil reservoir shall 
be capable of holding at least 25 gallons of additional fluid above 
the amount required moving the elevator safely to the upper floor. 
The motor must be insulated to withstand up to 120 starts per hour 
without burnout from overheating. The valve shall be installed 
inside the reservoir and under the reservoir cover. The valve must 
be mounted above the oil level. Provide a drain connection fitting 
near the bottom of the oil reservoir. A heater must be installed in 
the Oil reservoir to maintain constant hydraulic oil temperature.

9.	Hydraulic Cylinder Installation:

a.	All hydraulic cylinder casing for new hydraulic elevators or

replacement cylinders for existing elevators must be installed in a

completely plumb condition with a variation of not more than 1/8-inch 
variation from absolute vertical plumb condition from bottom to top 
of the cylinder. The plumb condition must be demonstrated to 
representatives of Florida State University and/or his/hers designee 
prior to installation of the back fill sand, and prior to installation of 
the guide bearing and plunger assembly in the cylinder. A weighted 
“spider” shall be hung from a plumb line for checking the plumb 
condition at least every 12 inches from bottom to top of cylinder.

The back-fill material for the hole surrounding the hydraulic 
cylinder must be washed masonry sand only. Building rubble, 
wood, steel, concrete, rocks or any other debris will not be 
permitted to be dumped into the hole surrounding the cylinder

All hydraulic cylinders for new hydraulic elevators or

replacement cylinders for existing elevators must be fully protected by schedule 40 PVC piping and 100% isolated from all other portions of the elevator, building, pumping unit and the pit floor.

Copper tubing (2 tubes, ¼ inch interior diameter) must

be installed to be used for checking for liquid presence in the    space between the PVC pipe and the pressurized cylinder

one (1) copper tube shall be approximately 30 inches

long and equipped with a quick-connect fitting to allow low-pressure air 
hose to be attached. Air pressure will be applied to the PVC pipe for 
purposes of determining if the liner contains either water or oil. Install a 
cap on the fitting to prevent dirt, debris, oil or water from entering the 
PVC liner. One (1) copper tube shall be long enough to run from the pit 
area to within ½ inch of the bottom of the PVC liner. Extend the tubing so 
that it does not interfere with any of the pit mounted equipment or 
elevator car but to a point that it could be used later to check for any

76

liquid that may have accumulated in the bottom of the PVC liner. Install a screw type cap on the upper end of the tubing to prevent dirt, debris, oil or water from entering the PVC liner.

Seal the space between the pressurized cylinder and PVC pipe, at least six

(6) inches deep, with oil resistant RTV (Room Temperature Vulcanizing) Silicone Sealant. The cylinder must be electrically isolated from all other components that would permit an electrical path to ground.

Cylinder must be primed and receive two (2) coats of	machinery

enamel prior to installation inside the PVC pipe.

XV.	TRACTION ELEVATOR:

NOTE: ALL TRACTION ELEVATORS MUST BE INSTALLED

ACCORDING ALL CODES AT THE TIME OF INSTALLATION.

1. 	All elevator driving machines and elevator controller

equipment must be Installed in a machinery room separate from the hoist way area.

2. 	All new or up-graded geared traction driving machines

must have full synthetic gear oil of the proper viscosity according to the machine manufacturer‘s recommendation.

1.	Traction elevators must have VVVF AC controllers with digitally controlled ―closed-loop‖

type vector controlled micro-processor systems

such as Megnetek. The motor control system shall be quiet in operation with no objectionable air-borne or electrical noise.

4. 	All traction elevators must be equipped with as ascending elevator-braking

system. The system shall be or equal to a Hollister-Whitney rope gripper system, a counterweight safety device with over-speed governor or a bi-directional undercar safety device/over-speed governor.

5.	Provide access door leading to metal gratings that shall be provided in shafts,

where required by code, to permit access for lubrication of sheaves and

equipment.

6.	Provide highly accurate electronic load weighting device, overload alarm

and signal light. Alarm and signal light shall function if load exceeds

design capacity. Elevator shall not function if overloaded conditions exist.

7.	All door frames, headers, etc., shall be grouted solid to maintain fire

rating.

77

XVI.	HOLE LESS EQUIPMENT:

If Hole less type of equipment is to be installed, isolation from the building is a must.

Place the piston that will be installed in the pit on Non-Conductive and Non-Compressive material. If guide shoes are used, the guide shoes must be of the Non-Metallic type. 
Isolation material must be used to ensure that all hydraulic piping does not come in 
contact with the building.

XVII.	CABS:

1.	If applied Wall Panels are used, place the Wall Panels on the sides and/or rear of

the Elevator Cab; the panels must be constructed of 3/4‖ thick quality A/B grade 
plywood. The panels shall be backed with plastic laminate material to reduce 
warping and moisture intrusion. The face of the new panels shall be covered with 
a high quality plastic laminate (.50 thickness, minimum) in color and texture as 
selected by the Owner. Apply type no. 316 L, No. 4 satin finished stainless steel 
angle edges on the panels with mitered and welded corners. The stainless steel 
panel binders shall be formed of 10 gauge angles with screw attachments on the 
rear of the panels. The distance between the panels shall be reduced to 
approximately 1‖. Attach the new panels in a manner that requires a workman on 
top of the car to remove fasteners to prevent easy removal by unauthorized 
personnel.

Cover the area surrounding and between the panels, as well as the base area, with 
Type 316 L, 16 gauge satin finished stainless steel glued to the cab‘s backing 
panel.

Over-lap the spaces by a least 2‖ on each side to prevent the stainless steel from 
becoming dislodged once the panels are in place. Use the highest quality 
industrial contact cement for attaching the stainless steel to the reveal areas.

1. 	Provide a complete set of protection pads and stainless steel protection pad

buttons on each panel and on front return panel. Install the pad buttons with ‖locktite‖ to prevent easy removal.

2.	Elevator Cab‘s floor shall be of resilient floor tile or vinyl sheeting.

Carpeting shall not be used. Diamond plate of Stain-less steel material

shall be used in special areas.

4. 	The Elevator Cab‘s for new or up-graded elevators must have hinged, swing type

front return panels to contain all of the operating devices, stainless steel vandal 
resistant buttons, indicators, standard size certificate holder, emergency phone 
(furnished by OTC), handicapped markings and other devices. NO SEPARATE 
COVER PLATES FOR CAR OPERATING STATION WILL BE ALLOWED.

78

All mounting must be from the rear to provide neat and vandal resistant panel. All information is to be engraved into panel. No plates or covers shall be attached from the front of the panel.

Front return panels must have heavy hinges, and vandal resistant locking devices.

The car operating panel shall contain all buttons and operating devices

require by A17.1. Any other switches such as car lights, exhaust blower,

Independent service, etc. shall be located in a separate cabinet with a locked, hinged door.

All stainless steel in elevator cabs for dormitories shall be 14 gauge, Type 316L 
stainless steel, except when heavier gauges are required for the application.

5. 	Cab ceilings for passenger elevators must contain either ―down-light‖ type

lighting with vandal resistant security rings and electronic dimmers, or

suspended ceiling with Lexan  ―Thermoclear‖ panels in 11 gauge stainless

steel frame. Cab lighting must measure at least 35-foot candles at the elevator floor near the cab entrance threshold with the door open.

6. 	All elevators must have cab emergency lights and alarm System that is at least

equal to Elevator Product Corporation ―Flexilite‖- EFP1 system that will

illuminate a portion of the normal cab lighting fixtures for at least four (4) hours. System must have four (4) gel cell six (6) volt batteries and a charger-inverter unit, all for mounting on the car top.

7.	The passenger or service elevator door protection must be Janus Pana 40    Plus,

with 3-Dimenisional-protection feature.

1. 	Install a top emergency exit as required by ASME A17.1 Safety Code for

all Elevators. Include electrical contact arrangement to prevent the elevator for being operated unless the top emergency exit is in the closed 
and locked position.

XVIII. ELEVATOR PHONE:

1.  A one (1) inch home-run conduit shall be provided from the elevator phone to the telephone 
	equipment room.

2. 	Elevator  Contractor  shall  provide  and  install  phone  that  meets  the 
requirements of the FSU Office of Telecommunications (OTC).  The phone shall 
be rear mount in a swing type return panel;   provide a punched or drilled grille work for the speaker and microphone. Each elevator shall have an emergency telephone. Programming and Wiring

connections shall be accomplished by OTC.

79

XIX  CAB DOORS:

In Dorms, all Hoistway Door emergency release escutcheons shall be equipped with

Barrel Key locks as manufactured by Tri-lock  Mfg. And Maint. Corp. using Barrel Key 
#6950.

XX. FREIGHT ELEVATORS:

NOTE: ALL FREIGHT ELEVATORS MUST BE INSTALLED

ACCORDING ALL CODES AT THE TIME OF INSTALLATION.

9. 	Freight elevators shall be located in close proximity to docks and service area. They shall 
go to each floor and be of sufficient size to accommodate large equipment.

2. 	In the event a freight elevator is installed in a corrosive environment or

installed in conditions that require sanitary environment, the equipment shall be 
fabricated from extremely corrosion resistant and/or materials that are easily 
sanitized.

3.	If power assisted car gate(s) is used, provide electronic screen across gate

opening.

4.	Provide highly accurate electronic load weighting device, overload alarm

and signal light. Alarm and signal light shall function if load exceeds

design capacity. Elevator shall not function if overloaded conditions exist.

5.	All door frames, headers, etc., shall be grouted solid to maintain fire

rating.

XXI.	CHAIRLIFTS:

NOTE: ALL CHAIRLIFTS INSTALLED ACCORDING ALL CODES AT THE 
	TIME OF INSTALLATION.

Any chairlift being placed outside of building must be manufactured

to withstand WET conditions and be placed in surroundings to protect from ALL weather conditions.

XXII. 	DUMBWAITER:

NOTE: ALL DUMBWAITERS MUST BE INSTALLED ACCORDING ALL 
	CODES AT THE TIME OF INSTALLATION.

80

The Dumbwaiter Car shall be constructed in Stainless Steel, including the Bi-parting car gate. Car shall have a least one (1) Stainless Steel Shelf. Hoistway Doors, Hoistway Frames and Door Seals shall be Stainless Steel.

XXIII. APPROVED MANUFACTURERS

1.	Approved Elevator Manufacturers:

a.	ThyssenKrupp Elevator Corporation

b.	Otis Elevator Company

c.	Schindler Elevator Company

2.	Closed-Loop Door Operator Equipment

a.	MAC

b.	ECI

c.	Motion Control Engineering

d.	Smartraq

e.	Approved elevator manufacturers‘ proprietary equipment

subject to the requirements of Sections VII, VIII and XXIV.

3.	Micro-Processor and Car/Group Control Equipment

a.	Motion Control Engineering and Elevator Controls Corp.

b.	Approved elevator manufacturers‘ proprietary equipment

subject to the requirements of Sections VII, VIII and XXIV.

4.	Motor Drive Systems for Elevator Machine Motors

a.	Megnetek

b.	Approved Equal

5.	Hoisting Machine Motors Only

a.	General Electric

b.	Imperial Electric

c.	Magnetek

d.	Rueland Electric

e.	Approved Equal

6.	Elevator Hoisting Machines and Deflector Sheaves

a.	Hollister - Whitney Elevator Corp.

b.	Titan Machine Corp.

c.	Approved Equal

7.	Rope Gripper for Traction Machines

a.	Hollister - Whitney Elevator Corp.

b.	Approved Equal

8.	Hydraulic Fluid

81

a.	Hydro Safe Oil Division, Inc., Grade ISO VG-32

b.	Approved Equal

9.	Pump Motor

a.	General Electric

b.	Imperial Electric

c.	Magnetek

d.	Ziehl-Abegg

e.	Thyssen/Krupp

f.	Approved Equal

10.	Hydraulic Pump

a.	IMO

b.	Allweiler AG

c.	Approved Equal

11.	Oil Control Valves

a.	Beringer

b.	Maxton

c.	EECO

d.	Thyssen/Krupp

e.	Approved Equal

12.	Hydraulic Cylinders

a.	EECO

b.	United

c.	CEMCO

d.	Approved Equal

13.	Pipe Rupture Valves

a.	EECO

b.	Thyssen/Krupp

c.	Approved Equal

14.	3D Door Detector Devices

a.	Janus Elevator Products

b.	Approved Equal

15.	Car Emergency Lighting System

a.	Elevator Products Corp.

b.	Approved Equal

16.	Vandal Resistant Signal Fixtures

82

a.	Innovation Industries

b.	GAL

c.	EPCO

d.	Thyssen/Krupp

e.	Schindler

f.	Otis

g.	Approved Equal

17.	Battery Powered Automatic Lowering System

a.	Reynolds and Reynolds Electronic

b.	GAL

c.	Schindler

d.	Otis

e.	Approved Equal

18.	Elevator Cab Materials

a.	Gunderlin, Ltd.

b.	Tyler Elevator Products, Inc.

c.	H&B Elevators

d.	Elevator Cabs, Inc.

e.	Approved Equal

19.	Elevator Hoistway Entrances and/or Hoistway Door Panels

a.	Gunderlin, Ltd.

b.	Tyler Elevator Products, Inc.

c.	H&B Elevators

d.	Elevator Doors Inc.

e.	Approved Equal

20.	Guide Shoes and Roller Guides

a.	Elsco

b.	Thyssen/Krupp

c.	Otis

d.	Approved Equal

21.	Paint & Coatings

a.	Pratt & Lambert

b.	Sherwin-Williams

c.	Martin Senour

d.	Approved Equal

22.	Chairlift Manufacturers

a.	National - Wheel - O - Vator Inc.

b.	Porch Lift

c.	Approved Equal

83

23.	Dumbwaiter Manufacturers

a.	Atlas Elevator Company

b.	Matot Corp.

c.	Approved Equal

24.	Door Hanger and Interlock Equipment

a.	GAL Manufacturing

b.	Approved Equal

25.	Mobil Computer Security Cabinet

a.	EDSAL #CSC6726

b.	Approved Equal

XXIV. APPROVED SUBSTITUTIONS

1. 	Where noted in Section XXIII, the Elevator Contractor may request

approval of substitutions. Substitutions must, in the opinion of the Owner, Architect and Elevator Consultant, equal to, or exceed, the quality of 
the specified product.

2. 	Where  noted  above,  products  manufactured  by  the  list  of  Approved

Elevator Manufacturers  will  be acceptable subject  to  complete compliance with the technical specifications written based on these guidelines.

3. 	Elevator Contractor may only substitute other manufacturers of

Elevators Cabs and Elevator Hoistway entrance materials, subject to the following:

a. 	The Elevator Contractor must agree to an inspection by the Owner‘s

Representative(s), Architect and Elevator Consultant (if used on project) 
of the Elevator Cabs and/or Elevator Hoistway Entrance materials at the 
factory after shop assembly, but prior to shipment to the project site. 
Any deficiencies found after assembly at the factory shop must be 
corrected prior to shipment to the installation site. The Elevator Contractor 
shall schedule the shop inspection at least 20 days in advance of the 
physical inspection date to allow suitable arrangements to be made for 
inspection of the materials.

b. 	The substitution(s) must fully comply with the specifications

contained herein, including design, quality of fabrication and fit, quality of materials and every other aspect of the specified products.

c. 	The Elevator Contractor shall be responsible for all costs

associated with correcting any deficiencies, or deviations

84

from the specifications, caused by substitutions of material

that is specified herein. Further, the Elevator Contractor shall be

responsible for arranging for all travel time and costs of Architect and

Elevator Consultant (if used on project) associated with visiting, or

revisiting, the manufactures facilities to examine the work of any firm not on the approved bidders list.

d. 	No extension of time in the completion schedule for the work will be

granted as a result of the need to correct defects or deficiencies associated with the use of material substitutions.

END OF SECTION

85

DIVISION 15 - MECHANICAL UTILITIES AND EQUIPMENT

All utility work shall be coordinated with and approved by the Utilities Section through the Project Manager. Explicit details shall be shown for all connections to existing utilities.

Utility work and connections to University utility systems must be properly planned to prevent disruption of classes, 
research efforts or life in the Residence Halls... All utility work shall be coordinated with the Utilities Section 
through the University Project Management Section. Each drawing that shows a connection to existing utilities must 
have a note that states that the Contractor shall request permission for all outages as far as possible in advance. This 
shall be a minimum of 14 days except in case of emergency. It shall be noted that even with the advance notice, it 
will not always be possible to grant the requested time and date, as classes and research must have precedence. 
Permission must be obtained, through the project manager, from the Utilities Section. Explicit details must be shown 
for all connections to existing utilities. The Utilities Section must approve both the location and method of the 
proposed connection, in advance... Note: this applies both to temporary construction utility connections as well as 
the permanent utility connections.

1. 	It shall be the responsibility of the A/E to investigate and determine the actual location of all underground 
	utilities or obstructions at the building site before beginning design work. The University will provide all 
	available information as appropriate.

2.	The construction contract specifications shall provide for the orientation and training of University personnel on

all installed equipment and systems.

3. 	The contractor shall pay for utilities during construction. The contractor shall contract with the City of 
	Tallahassee whenever possible. If it is necessary to have construction utilities supplied from the University, the 
	contractor shall install temporary services in accordance with local codes. The University will bill the contractor 
	monthly for utilities used. Shall the University wish to make an exception to this; the A/E will be so informed.

4. 	Heat, air conditioning, humidity control and any other environmental factors shall be the responsibility of the 
	contractor throughout the construction period.

5 The Architect/Engineer shall conduct a life-cycle cost analysis of alternative architectural and engineering designs 
to evaluate the efficiency of energy utilization for competing designs in the construction of new buildings.   These 
requirements also apply to major building renovations the replacement of major energy consuming equipment in 
existing buildings. The University Project Manager will advise the A/E as to the time during the Design that this life 
cycle analysis is due.

(2)  Such life-cycle costs shall be the sum of:

(a)  The reasonably expected fuel costs over the life of the building, that are required to maintain illumination, power, temperature, humidity, and ventilation and all other energy-consuming equipment in a facility, and

(b)  The reasonable costs of probable maintenance, including labor and materials, and operation of the building.

(3)  To determine the life-cycle costs the analysis shall include, but not be limited to:

(a)  The orientation and integration of the facility with respect to its physical site.

(b)  The amount and type of glass employed in the facility and the directions of exposure.

(c)  The effect of insulation incorporated into the facility design and the effect on solar utilization of the properties of external surfaces.

(d)  The variable occupancy and operating conditions of the facility.

86

(e)  An energy consumption analysis of the major equipment of the facility's heating, ventilating, and cooling system, lighting system, hot water system, and all other major energy-consuming equipment and systems as appropriate. This analysis shall include:

1.  The comparison of alternative systems.

2.  A projection of the annual energy consumption of major energy-consuming equipment and systems for a range of operation of the facility over a 25 year life of the facility. The analysis shall include the replacement costs of major equipment that has a life expectancy of less than 25 years.

3.  The evaluation of the energy consumption of component equipment in each system, considering the operation of such components at other than full or rated outputs.

(4)  The Architect/Engineer shall prepare data, make the input and run the analysis on an appropriate Life-Cycle Cost Computer Program such as the Trane Trace Ultra 600, Carrier HAP 3.0, Elite Software‘s Energy Program or other program based on DOE standards and approved by the University.

(5) Before preparing the data, the Architect/Engineer shall discuss the energy-saving schemes proposed for the 
Project with the university Project Manager. The Architect/Engineer shall submit two sets of the following to the 
Owner: cover letter discussing the energy saving schemes considered, the computer results, the Architect/Engineer's 
recommendations and discussion of other energy-saving measures incorporated into the Project design, copy of the 
university Project Manager's written concurrence with the schemes and the complete computer run printout.   The 
university Project Manager will notify the Architect/Engineer of the approved scheme to incorporate into the project.

5. 	All utilities are to be metered for each building, including water, steam, and chilled water. All utility metering 
	must be coordinated with the University Project Manager prior to construction. All metering devices must have 
	the capability to report to the Campus Energy Management System. If the building contains Auxiliary 
	occupants in addition to E&G occupants, separate metering must be provided for each Auxiliary occupant. This 
	shall be coordinated with the Utilities Section through the Project Management Section.

6. 	Provide separation of mechanical equipment and other noisy areas from academic and office areas.

7. 	Care shall be taken in the placement of all outdoor air inlets to ensure that odors and other pollutants 
	(automobile exhaust, generator exhaust, fume hood exhaust, etc.) do not enter the building.

8. 	Mechanical rooms must have adequate openings to facilitate the removal and replacement of major pieces of 
	equipment. Provide double 3'-0" doors which swing outward, with active/inactive leafs.

9. 	There must be adequate space in mechanical rooms to provide ample access space around all equipment for 
	routine maintenance items and procedures, such as filter replacement, lubrication, and so on.

10. Pipe insulation thickness to be per latest energy efficiency standards.

12. Access to electrical rooms,  mechanical rooms, telephone closets, elevator machine rooms, fan rooms,

87

Pump rooms, etc., shall not be through other rooms. It is preferred that access to these spaces be achieved from a main corridor and/or exterior space. Access shall not be by ladders. Where possible, penthouse rooms shall have elevator access.

13. Mechanical Rooms and similar spaces are not to contain storage areas. All power disconnects to equipment shall 
	be so located as to be easily accessed.

14. All piping shall be color coded and labeled as to use.

15. All fans shall be labeled as to use, area served and power source.

16. All HVAC controls shall be of the direct digital type and conform to the standard outlined in Appendix D -
	Building Automation and Central Monitoring Systems.

17. All hydronic systems shall have adequate air eliminators installed.

18. Provide MERV 9 air filtration on all central-station air handling units.

19. Manhole design shall be carefully coordinated with the University Project Manager and the Utilities Section. 
	Contact Director of Utilities for latest manhole standards.

20. All piping utilized for underground piping are required to have the ends sealed prior to storage or use on site. No 
	end seals shall be removed until the end in question is actually ready for welding or otherwise connecting. In no 
	event shall any piping be left in a trench with an open end at any time. This requirement shall be strictly 
	enforced.

21. Systems Test & Balance will be provided through the A/E as an additional service. The specifications will 
	require the contractor to participate in the testing, make any changes necessary and pay for any re-testing that 
	may be required to make the systems meet specifications.

22. All air handling unit condensate drain pans must drain to the storm sewer system, with a by-pass to the floor 
	drains when using chemicals to clean coils. Contract Director of Utilities for standard detail for coil drains.

23. Mechanical rooms shall not be utilized as return air plenums.

24. Mechanical rooms that generate heat such as steam rooms and pump rooms shall be cooled using a 
	thermostatically controlled forced air ventilation system utilizing outdoor air. Generally, pump rooms and 
	similar spaces with electronic systems such as variable speed drives, shall be separated from rooms containing 
	steam reducing stations and condensate pumps. Wherever possible, intake air shall be directed into the pump 
	room and removed from the steam room. If cooling using outdoor air is considered not feasible, approval of an 
	alternative cooling scheme shall be approved by the Director of Utilities.

25. All mechanical equipment such as air handlers, pumps, exhaust fans, etc., shall be referred to and labeled by 
	floor number, i.e., EF3-5 would be the fifth exhaust fan on the third floor.

26. The A/E shall contact the University Department of Environmental Health and Safety Asbestos Coordinator 
	prior to the commencement of a renovation project in order to determine the specifications for labeling and 
	demarcation of the extent of new (non-asbestos) pipe insulation applied by the mechanical contractor following 
	any abatement of asbestos pipe insulation for the project.

27. Identification signage systems and markings for all mechanical equipment and piping shall be required.

28. For additional requirements of specific FSU classroom types - see Appendix E.

PLUMBING

1.  The City will furnish water meters and taps for domestic and fire water. All tap fees and system charges shall be 
	paid for by the Contractor. The City of Tallahassee has jurisdiction over the installation. Install water meters 
	and domestic water backflow preventers above grade and provide insulated cover. Install backflow preventers in 
	accordance with City Ordinance. Contact the City for their requirements and information The City's approval 
	for all proposed connections must be received prior to completion of the 100% documents. Written proof of the

88

City's approval must be provided to the Utilities Section prior to bidding the project. Fire Flow backflow preventers shall be installed inside the building.

2.  Below grade, all domestic cold water piping exterior to building shall be ductile iron or PVC. Underneath 
	buildings, piping shall be type K copper or ductile iron. All domestic water piping inside the building and above 
	grade shall be type L copper, except for high purity water. Materials for high purity water systems shall be 
	coordinated with the University Project Manager.

3.  Floor drains are to be provided in all toilet rooms, custodial closets and mechanical rooms.

4.  All piping system strainers shall be equipped with valves for blowdown cleaning.

5.  Hose bibs shall be provided in toilet rooms located underneath the sink, machinery rooms and at 100-foot 
	intervals in exterior areas for maintenance use.

6.  Teflon containing joint sealer shall be utilized in all screwed piping installations.

7.  All piping shall be color coded and labeled as to use and flow direction.

8.  All exterior valves shall be fitted with a complete one-piece valve box unit constructed of concrete, steel or 
	plastic. The box shall have a hinged cover and be set in concrete. The installation shall be such to support small 
	vehicle and lawn maintenance equipment.

9.  Urinals shall be of the flooded open throat type to avoid stoppages and odor problems. Urinals shall be provided 
	with automatic flushing sensors. Urinals shall be designed for 0.13 gallons per flush.

10. Floor drains, where necessary, are to be placed at the lowest point in the area and shall be provided in all 
	restrooms, custodial closets, mechanical rooms, storage rooms, etc.

11. Lavatory faucets shall be the types that will not flow over 0.5 GPM and provided with automatic sensors. Where 
	sensors are not considered cost effective, timed shut off valves shall be used.

12. Standard type washbasin shall have strainer type drain, lever handles equipped for handicapped use, cold water 
	faucets, no hot water faucets (except in dormitories and service buildings) and soap dispensers.

13. Water Closets shall be wall mounted and designed for a maximum of 1.24 gallons per flush.

14. Custodial closet faucets shall be single delivery mixing type with hot and cold water and have threaded spout 
	equipped with a vacuum breaker and a three-foot hose. Place faucets 30" - 36" above sink rim.

15. In new facilities, provide at least one drinking fountain which includes a bottle refilling station.   This unit 
	should be located on the ground floor and be readily accessible from the main entry.   Installation should be 
	ADA compliant.

WATER BASED FIRE EXTINGUISHING SYSTEMS (Where required)

1. 	The contractor shall furnish all labor and equipment for the complete installation of a water based fire-
	extinguishing system and shall be the installing contractor or site representative with the required license. No 
	subcontracting will be allowed. The contractor must be NICET level III certified and must possess the 
	appropriate class I or class II fire sprinkler license as required by the State of Florida.

2. 	Fire water based systems shall be installed, inspected, tested and certified per appropriate NFPA 13, 14, 20, 24, 
	25, including NFPA 101. Any applicable codes shall apply to meet State of Florida and Fire Marshal 
	requirements, local and state jurisdiction.

3. 	The fire system contractor shall be responsible for equipment, materials and workmanship of the system for one 
	year. The warranty shall be enforced 24 hours a day, seven days a week including weekends and holidays 
	during this period of time. The contractor will also respond after being advised of his responsibility and the 
	nature and/or condition of the equipment that has failed by the FSU Fire Systems on-call technician. After

89

notification has been made to the responsible equipment contractor, a minimum of one hour will be allowed to respond and arrive on site. When the problem has been secured or corrected to the satisfaction of the technician o the FSU Police Department will be notified.

4. 	The installation of fire water mains shall included backflow preventers in accordance with NFPA 
	requirements including local City Ordinance. Contact them for their requirements and information. All fire mains 
	and/or valves shall be painted and labeled to indicate the proper building name controls. The City must approve 
	all connections to the City water mains. The City's approval must be received prior to completion of the 100% 
	documents. Written proof of the City's approval must be provided to the Utilities Section prior to bidding the 
	project.

5.	Fire water system connections and fittings shall be compatible with the City of Tallahassee Fire Department

fittings. Contact them for information.

6. 	Provide six extra Escutcheon Plates of each type installed on any system, installer will provide manufacturer 
	name and address, supplier name and address and parts number.

7. 	The main drains and inspectors test drains be piped to an adequate drain or outside the building. When piped 
	outside the drain shall not affect the architectural design and landscaping of the building. When piped outside 
	the building, the water flow shall not pose a threat to persons on sidewalks or streets adjacent to the building.

8.	Provide 3-1/2" gauges with a connection not smaller than 1/4", and each gauge connection equipped with a

shutoff valve and provisions for draining.

9.	All control, drain and test connection valves shall be provided with permanently marked weatherproof metal or

rigid plastic identification signs. The sign shall be secured with corrosion-resistant wire, chain or other approved

means.

10.	All control valves will have proper signage to indicate the areas of coverage. This will start from the feed

supply into the building through all branch lines.

11.	On any fire pump installation, the use of PVC and/or plastic pipe, fittings, or components will not be acceptable.

HEATING AND STEAM

1. Steam is supplied at pressures varying between 70 psig and 125 psig, depending on the season. The building 
	steam systems shall have a minimum utilization pressure of 50 psig and shall be designed to operate with the 
	inlet pressure to the building varying between 70 psig and 125 psig.

2.  All bolts and nuts shall be hex configuration, coarse threaded, and be of ASTM A-193, Grade B7 alloy steel 
	such as USS Supertanium alloy, or equivalent.

3.  All high pressure and low pressure steam piping shall be Grade A ASTM A-106, schedule 40 seamless piping, 
	and condensate return lines shall be schedule 80 seamless pipe. The use of pre-insulated steam and condensate 
	return piping is permissible. Contact the Director of Utilities for currently approved types and manufacturers.

4.  All steam and steam condensate lines underground shall have properly sized expansion loops, which shall be 
	properly anchored. If pre-insulated piping is used, the expansions loops shall be sized and located per 
	manufacturer's instructions.

5.  Valves installed above grade as part of the high-pressure steam system, and valves installed below grade, shall 
	be 300 lb. valves. Valves that are 2-1/2" and larger shall be flanged, and all valves less than 2-1/2" shall be 
	screwed. Valves installed in manholes shall be 300# butterfly valves. Contact Director of Utilities for latest 
	approved types.

6.  All piping that is 2-1/2" and larger shall be welded, not screwed. A certified welder shall weld all underground 
	fittings.

90

7.  High pressure steam fittings 2" and larger shall be butt-welded fittings with backing rings. Fittings that are 1-
	1/2" and smaller shall be forged steel screwed or socket weld fittings. Unions that are 2" in size shall be 300 lb. 
	screwed cast iron or forged steel. All high-pressure steam nipples shall be schedule 80.9. Low pressure steam 
	fittings that are 2" and larger shall be schedule 40 butt welded fittings with backing rings, and flanges shall be 
	slip-on or weld neck flanges. Low pressure steam fittings that are 1-1/2" and smaller shall be 150-lb. cast iron 
	using 300 lb. cast iron unions and schedule 40 nipples.

8.  Condensate lines that are 2-1/2" and larger shall be schedule 80 butt weld fittings with backing rings and steel 
	weld neck or sip-on flanges that are the same pressure class as the valves. Condensate lines that are less than 2-
	1/2" shall be forged steel or socket weld using 300 lb. screwed unions and schedule 80 nipples.

9.  All steam condensate receiver unit vents shall be run full size from unit to a safe discharge location. In no case 
	is the discharge to be over a sidewalk or other public area. In addition, discharges shall not be located near air 
	intakes.

10. Insulation for high and low pressure steam and condensate lines above grade shall consist of calcium silicate. 
	Below grade steam lines shall have a calcium silicate inner layer and a foamglas outer layer wrapped with glass 
	fabric cloth and with proper mastic applied. Condensate lines below grade shall have foamglas insulation 
	wrapped with glass fabric cloth and with proper mastic applied. Deviations from the above shall be approved by 
	the Project Manager.

11. The attachments for the insulation below grade shall be stainless steel wiring or bands, or 16 gauge copper wire, 
	on 9" centers.

12. Below grade steam fittings are insulated with mitered segments of calcium silicate wired in place. Below grade 
	steam flanges, unions, and valves are insulated with oversized pipe insulation.

13. All insulation materials shall be installed according to the manufacturer's instructions.

14. Inside buildings, all domestic hot water piping shall be insulated with foamglas pipe insulation and the domestic 
	cold water piping that is exposed in unconditioned spaces shall be insulated to prevent sweating.

15. All water valves that are 2-1/2" and larger shall be flanged 125 psi valves. All pressure and temperature gauges 
	shall be 4-1/2" face, bottom connection, and industrial grade.

16. All temperature gauges shall be mounted in wells.

17. All steam pressure reducing valves shall be Fisher, pilot operated. Contact Director of Utilities for currently 
	approved alternates.

18. Refer to Building Management System/Remote Control Monitoring Appendix D, for Steam Flow Metering 
	requirements.

19. All condensate pumping units shall be above grade and shall be duplex electric pumps with cast iron receivers 
	and ceramic seals, or with the approval of the Utilities Section, may be of the steam pressure type. The pumps 
	shall be equipped with balanced mechanical seals.

20. All water pumps shall be equipped with balanced mechanical seals.

21. Utilize the campus steam system as a heating source with a pumped condensate return to the Central 
	Utilities Plant.

22. Install drip traps before all thermostatic temperature-regulating valves and pressure reducing valves.

CENTRAL UTILITY PLANT (CUP) CENTRAL CHILLED WATER SYSTEM/BUILDING INTERFACES

1.  The following are requirements for new building designs in order to best produce the most efficient utilization 
	of the Central Utility Plant (CUP) system, utility distribution system, and the building.

91

2.  The Central Utility Plants are designed as a variable flow system to achieve maximum energy economics. The 
	design of the building shall be such as to operate over a varying pressure range.

3.  The interface between the building and the Central Chilled Water Distribution System shall insure the chilled 
	water temperature difference will equal to or exceed 15 degrees while satisfying the building design criteria. 
	The interface will also insure that the building pump(s) and the distribution pump(s) will be completely 
	decoupled. The Utilities Section will provide design and material requirements for the interface.

4.  The CUP is operated to produce 45 to 48 degrees F. chilled water depending on overall system needs and 
	energy conservation measures being utilized. The design professional shall verify this strategy with the project 
	manager before design begins.

5.  Existing pressures leaving the CUP vary from 50 to 85 psig. Be aware that the maximum operating pressure for 
	the existing chilled water underground piping is 100 psig. Any additions to this system shall be designed for 150 
	psig.

AIR CONDITIONING

1. 	Utilize the campus chilled water system for cooling if at all possible. The interface between the system and 
	building is discussed later. A fine mesh monel or stainless steel strainer shall be installed in the chilled water 
	supply line of each building to prevent contamination of the building chilled water system. All chilled water 
	strainers shall have a pressure gauge installed across the strainer so as to quickly determine when strainers are 
	dirty.

2. 	When the air conditioning system cannot be connected to the Central Chilled Water System, consider the use of 
	water cooled condenser(s) utilizing a deep well water supply with injection return. Utilize existing wells as 
	practical. New well pumps shall be mounted above ground with a suitable enclosure. Provide water lubrication. 
	Cooling towers are not desired by the University. The existing Northwest Florida Water Management District 
	Consumptive Use Permit will have to be amended if a new well is to be installed. Be aware that Leon County 
	has a Wellhead Protective Ordinance that also will have to be complied with. All cooling well design and 
	permitting must be coordinated with the Utilities Section.

3.	All air conditioning condensate lines shall be of insulated type "L" copper or approved equal. Provide insulation

details to insure vapor proof covering.

4. 	If condensation occurs on the outside of insulated ducts, HVAC equipment, VAV boxes, flex ducts, piping, etc. 
	during the construction period, the Project Team shall take immediate action to determine the reasons, and 
	initiate corrective action. Substantial Completion shall not be approved until corrections are agreed to in writing. 
	The contractor shall be required to rework the insulation until satisfactory if condensation occurs on any cold 
	surface at any time during the warranty period.

5. 	All chilled water taps into the Central Chilled Water System shall be made without system interruption, where 
	feasible. Each juncture shall be provided with a shut off valve and valve box for easy access. Note that most of 
	the Central Chilled Water System piping is constructed of asbestos bearing material, i.e. Transite. "Hot tapping" 
	details will be provided by the University. All chilled water connections, whether external or internal, must be 
	coordinated with and approved by the Utilities Section. Initial coordination concerning the approved location of 
	new connections must be done prior to completion of the Schematic Design Phase.

6. 	Exterior steel piping shall be schedule 40 black steel with welded joints. The use of pre-insulated black steel 
	pipe is permissible. Contact Director of Utilities for currently approved types and manufacturers.

7. 	Insulation for chilled water piping above grade shall consist of foamglas that is covered with a .016 inch thick 
	aluminum weatherproof jacket that has a factory applied integral vapor barrier. The foamglas shall be glued to 
	the piping. Fasten with aluminum bands located not more than 12 inches apart. Insulation below grade shall be 
	foamglas with Pittwrap cover.

92

8.  All building chilled water systems served from central chilled water shall be designed to have variable flow 
	characteristics compatible with the central system.

9.  All chilled water piping shall be installed with shut-off valves at each floor and at each AHU.

10. All major air handling unit coils shall be designed for not less than 15 degrees Fahrenheit temperature rise, and 
be provided with two way control valving.  The use of fan coil units is discouraged; however, if there is no other 
practical option they may be utilized upon approval of the Director of Utilities. It is recommended that they not be 
installed above the ceilings. Insure that adequate ventilation is provided per ASHRAE Standard 62-1981R.

11. If feasible any fan coil units shall be provided with ducted, pre-condition ventilation air.  The direct connection 
	of un-conditioned ventilation air to fan coil units is generally prohibited.

12. A/C Air Handling Units shall be double wall construction with a solid inner liner (no insulation exposed to 
	airstream).

13. Air Handling Units shall have fans mounted on internal vibration isolators (2" static deflection).

14. Air Handling Units shall have double wall insulated drain pan.

15. Air handling units installed in spaces exposed to outdoor air conditions (such as attics) must be sufficiently 
	insulated to prevent surface condensation.

16. In classrooms, the HVAC system shall provide an adequate rate of "fresh air" in accordance with ASHRAE 62.

FUME HOODS

See Appendix 1: “FSU Specifications for Systems and Safety Equipment associated with Laboratories and Hazardous Materials Storage or Usage Areas”

93

REFRIGERANT MANAGEMENT REQUIREMENTS

General Requirements

1. 	The contractor and mechanical engineering design professionals shall work with the University's Refrigerant 
	Manager, to identify specific requirements for each project and interpret requirements from this section as they 
	pertain to upcoming work.

2.	Mechanical engineering design professionals shall incorporate the requirements of this section in their

equipment and contract specifications.

3. 	Contractor shall be responsible and accountable for compliance with the EPA Clean Air Act (CAA) Section 
	608, 40 CFR Part 82 and any state and local codes for all refrigerant-related work. Contractor shall ensure that 
	all contractor employees are made aware of the content of these practices prior to beginning work on refrigerant 
	containing equipment.

4. 	Contractor shall provide only proper level EPA certified technicians using EPA certified and registered 
	recovery/recycle units to perform work on FO&M refrigerant equipment.

5. 	Contractor shall submit the following information prior to starting any work.

A list of all service technicians' names and EPA certification numbers and level of certification (copies of EPA Certification Cards are acceptable).

1. 	A list of all recovery/recycling units to be used and a signed statement that an EPA Recovery Unit Acquisition 
	Certification form has been sent to the EPA (a copy of the form is acceptable).

2. 	A signed letter/memo addressed to contractor employees that notifies contractor technicians to provide the 
	specified refrigerant related information written on a Refrigerant Compliance ManagerTM software Service 
	Order input form.

3.	Documentation and Record-Keeping

4.	Contractor shall provide service records with all required information to the Refrigerant Manager. A Service

Invoice that is only sent to accounts payable does not meet the requirement for site records.

5.	Equipment ID tag number

6.	Manufacturer and Model number

7.	Serial number

8.	Location of equipment

9.	Refrigerant type and Unit Charge

10. Date of service

11. Service, repair or disposal description

12. Quantity of refrigerant added

13. Quantity of refrigerant removed, recovered, recycled, reclaimed or disposed of

14. Quantity of lubricant disposed of, and method of disposal

15. Detailed information on any leaks discovered and repaired

16. Name(s) of EPA certified service technicians who performed work

94

17. EPA Certified and registered recovery/recycling units used on equipment

New Equipment Guidelines

1. All new equipment installed shall utilize non-CFC refrigerants. The goal is to limit the number of new alternative 
	refrigerants utilized on site. Standardizing and limiting refrigerant types will reduce maintenance and inventory 
	costs. The Refrigerant Manager and engineering shall work as a team to determine what refrigerants are 
	presently in use and set standards for all future refrigerant equipment purchases.  In addition, further 
	maintenance and parts inventory cost savings can be achieved by standardizing on equipment manufactures. 
	Service history and existing parts inventory shall be considered in this analysis and the recommendations 
	presented to purchasing.

New Equipment ID Tags

1. All new equipment shall be tagged with a FO&M Unit ID number as specified by the Refrigerant Manager. This 
	number shall be used as the equipment id number by the RCM software.

New Equipment Leak Testing

1.  All new equipment including: packaged equipment - factory charged, field charged, split systems or field-
	constructed systems with field installed refrigerant piping shall be leak tested prior to or during startup. The leak 
	testing process shall utilize the appropriate electronic leak testing equipment and shall be witnessed by the 
	(Refrigerant Coordinator) or a designated HVAC technician.

2.  The contractor or installing party shall submit a RCM Service Order form with notes verifying the leak testing 
	and results to the Refrigerant Manager.

3.  If a leak is detected the following shall occur:

4.  Notify the Refrigerant Manager.

5.  Document the leak on a RCM Service Order input form.

6.  Repair the leak.

7.  Document the action and procedures taken on the RCM Service Order form.

8.  Leak test to verify the leak was repaired.

9.  Schedule and provide a 30-day follow-up verification leak test with a HVAC team member.

10. Document follow-up leak testing on the RCM Service Order form.

11. Repeat the above process if follow-up leak is detected.

Demolition Procedure for Equipment Removed by Contractors

1. 	Contract language for any refrigerant handling work by contractors shall include requirement for contractor to 
	provide names of EPA certified technicians with their certification number and certification level who will be 
	performing the refrigerant equipment demolition and refrigerant recovery. An RCM Service Order Form shall 
	be filled out by the certified contractor technician and forwarded to the Refrigerant Manager.

2. 	If a properly certified contractor technician removes the refrigerant, the unit tagged as such and the RCM 
	service Order form has been submitted then a non-certified person may perform the actual demolition.

3. 	The contractor in contractor provided refrigerant recovery cylinders shall take ownership of the recovered 
	refrigerant and transport off site to a proper disposal company or certified reclaimer (Unless other wise directed

95

by the Project Team). The quantity removed from each unit and from the site shall be documented on the RCM Service Order form used for the actual recovery procedure.

In all cases the contractor technician shall tag the unit that the refrigerant was removed, as required by the Refrigerant Manager.

BUILDING AUTOMATION AND CENTRAL MONITORING SYSTEMS Refer to Appendix D.

FIRE ALARM SYSTEMS

BASIC  REQUIREMENT  FOR  INSTALLATION:  All  new  buildings,  and  buildings  undergoing  major renovations, shall be equipped with a complete fire alarm system which meets 2012 Florida  Accessibility Code for Building Construction and all other current code requirements. Provide all hardware necessary to tie-in with the existing campus monitoring and Emergency Mass Notification systems. Matching the existing addressable digital fire system in use in a facility is preferred.

COORDINATION:

1. Coordinate all installations with EH&S Fire Safety Section.

2.  To  insure  compatibility,  the  EH&S  Fire  Safety  Section  supervisor 	(or  supervisor's  designated

representative) shall be informed of the proposed type of fire alarm control panel.

LICENSING: All work on fire alarm systems shall be performed by an individual, or firm, licensed as an "Alarm System Contractor I" as required by Florida Statute 489.505(a), other parts of said Statute, and complies with all other licensing requirements of relevant codes and laws. Further, this individual or firm shall be either the prime constructor on such work or a subcontractor to the prime constructor.

PANELS:

1. Central Fire Control Panel: Provide programmable central fire control panel, voice evacuation type. A non-voice evacuation system may only be utilized with prior approval by EH&S Fire Safety section.  Fire control panel shall meet NFPA 72 detector sensitivity readout/printout requirements. A history of a minimum of 200 events shall be readable on the fire alarm control panel display (200 events for alarm and 200 events for trouble).

2. Annunciator Panel: Annunciator panel shall be located where the fire department will enter building. Annunciation panel shall duplicate all functions of the fire control panel.

3. Renovations: When the existing fire alarm control panel does not support the type of

renovation being performed in a building, a second (or third) fire alarm control panel shall be installed. The fire alarm control panels installed for the renovation shall be of sufficient capacity to handle the entire building when the existing fire system(s) is (are) changed.

4. Acceptable manufacturers: Existing equipment requiring interface may be Simplex 4010 or 4100U Voice Evacuation; Pyrotronic. New equipment shall be Simplex 4020 or 4100; Pyrotronics MXL or XLS Voice Evacuation, addressable.

PULL STATIONS: Pull stations shall be single action type. Glass rods for pull stations are discouraged. In 
housing units pull stations shall be equipped with a protective tamper shield. The protective tamper shield 
shall be a clear Lexan cover that emits a loud piercing noise when disturbed. The cover shall be battery

96

powered and shall silence itself by lowering and realigning the shield. Stopper II as manufactured by Safety Technology International, Inc. (STI), are acceptable covers. Protective shields shall only be used to protect pull stations from the elements, or in locations where vandalism is likely (such as next to exterior exits). They are not required throughout the interior of a building.

ALARM UNITS: Alarm units shall be combination audible alarm and strobe light. The audible alarm shall be a speaker, not a bell. Provide separate power for speakers, horns and lights, so that lights can be checked without sounding horn.

AIR HANDLING UNIT SHUTDOWN RELAY: The Air Handling Unit shutdown relay shall be supervised.

JUNCTION BOXES AND CONDUIT: All junction boxes on the fire alarm system shall be painted fire-truck red and all conduit shall be spot painted red.

CAMPUS MONITORING SYSTEM INTERFACE RELAYS: Trouble contacts shall be Normally Open; Alarm contacts shall be Normally Open. Provide a Keltron- Digital Alarm Communicator Transmitter (DACT) for digital, secondary reporting to the University Police. Consult EH&S Fire Safety Section regarding the manufacturer and model required. The project shall provide and program the communicator as directed by the EH&S Fire Safety Section.

DUCT-MOUNTED  SMOKE DETECTORS:  Duct  mounted  detectors  shall  be  mounted  in  a readily accessible  location.  If duct-mounted smoke detectors (system and non-system) are  not  immediately visible from  inside the mechanical room, then provide a remote, labeled L.E.D indicator for each detector, mounted in a convenient, visible location. Non-radioactive smoke detectors and duct detectors are preferred (i.e. photoelectric). Provide stand-alone, duct mounted smoke detectors where no fire alarm system is present. The operation shall be to shut down the unit, and provide notification.

(Inserted section below)

MAINTENANCE ITEMS:

1. Provide a spare parts kit that shall include one of every type of field device (one pull station, one horn, one strobe).

2. Any special tools, equipment, programming devices and cables needed to maintain or repair the system shall be provided.

3. All keys or tools provided with any devices from the manufacturer shall be given to the EH&S Fire Safety Section.

EXECUTION:

All equipment shall be installed to provide adequate access for service and repair.

On retrofit projects that involve adding to existing wiring, the Constructor shall exactly match

the colors of the new wiring with the existing.  All new wiring shall be installed in conduit unless approved by EHS Fire Safety Section.

97

The Constructor shall certify and tag the system after all modifications are made and prior to Substantial Completion:

The installer and the EHS Fire Safety Systems Electronics Shop shall test the fire alarm system before any renovation or modification is made. Any part of the system not working properly shall be noted or repaired before any construction begins.

Fire alarm conductors shall be color coded as follows: Horns: Red +, Black -

Strobes: (if separate) White + Purple -
Alarms: Blue + Yellow -

A/C Ventilation: Shut Down Brown + Orange -
Magnetic Doors: Pink + Grey -

Misc. Circuits: Violet + Tan -

Data line wiring shall be twisted shielded 18 gauge FPLP wire in a red jacket. All data wire shall meet current code requirements and manufacturer's specifications. Speaker wiring shall meet current code requirements and manufacturer's specifications, and have a different color jacket than the data wiring (minimum 18 gauge twisted shielded).

On renovations always remove existing wiring and install new, properly color coded wiring.

On renovations, in addition to the renovation prints and/or drawings, the existing prints are to be up-dated to include any changes.

Speakers and lights shall be provided in machine rooms and loft/attic areas that have mechanical equipment or work areas.

All connections shall be made on terminal strips. No more than two conductors under one connection. Wires on these terminals shall be labeled.

Programming of the fire alarm shall be as specified by the University. Consult with EHS Fire Safey Office (or other appropriate University maintenance department, if directed by 
the FSU Project Manager) concerning the requirements. Programming includes, but is not 
limited to: function keys, FAAP, software zones, etc.

All fire and smoke alarm sensors shall be re-settable.   Beam detectors are discouraged and must be approved by EHs Fire Safety.

Provide protection from damage caused by lightning and electrical surges.

98

OPERATION:

AIR HANDLING UNITS: Actuation of any fire alarm initiating device shall cause all air handlers in the building area affected to shut down. Air handling units shall shut down only in the area where the fire is detected or the area actually alarmed (floor above and below). Other air handling equipment shall remain on line. This shall not supersede any code requirement.

ELEVATORS: A reset procedure for resetting the elevators after an alarm shall be submitted.

TROUBLE SIGNAL: Trouble signal shall sound piezoelectric alarm on the fire alarm control panel.

STAND ALONE DUCT DETECTORS: Provide an enunciator panel to provide notification of trouble alarm and reset feature. Panel to be 120 Volts.

MAINTENANCE ITEMS:

1. Keys to the system and associated equipment shall be given to the EH&S Fire Safety Section when the system is accepted.

2. All spare parts, special tools, equipment, keys, etc. required for maintenance or operation shall be turned over to the EH&S Fire Safety Section when the system is accepted.

3. A copy of the field prints, drawings, and current revision of computer program, etc. shall be given to the EH&S Fire Safety Section when the system is accepted.

EMERGENCY NOTIFICATION AND WARNING (FSU ALERT)

BACKGROUND:

The Florida State University maintains a comprehensive emergency notification and warning system known publicly as “FSU ALERT.”  This system employs multiple technology and delivery methods to distribute alerts.  As the university constructs or renovates buildings, it is critical to incorporate elements of the FSU ALERT system, as appropriate.

INDOOR SIRENS:

All structures equipped with new fire alarm systems must include capability for voice-based mass notification. Fire panels must be capable of receiving line-level audio input from an external source.  Speakers must be capable of delivering voice audio.

Provide an “Indoor Siren Interface” (RTU-ISI) from American Signal Corporation – Model KIT-FAP-INTFCE, including message card and interface, enclosed in fiberglass box and wall mount.  The unit shall be manufactured by American Signal Corporation to include: Motorola CM200 UHF 25 watt radio (MCM-200-U); Motorola Radio Interface UHF (KIT-RRM); Lightning Arrestor, BA Feed, VHF, PL-259 (KIT-ARR-2); Antenna, UHF, 100 feet of coax omni-directional (KIT-OMNI-ANT-5).

Constructor shall coordinate with the Department of Environmental Health & Safety, Emergency Management Section prior to ordering or purchasing any equipment from American Signal Corporation.  EHS-EM maintains a master roster of unit numbers and tactical addresses which are required for manufacturing and programming by American Signal. EHS-EM must approve all Order Acknowledgement and Programming forms provided by American Signal.

The constructor shall mount the RTU-ISI adjacent to the fire alarm panel using the wall mounts provided by American Signal Corporation.  Provide 110V AC electrical power to the RTU-ISI.  Mount the antenna on the highest external vertical surface (exterior wall) possible given the 100 feet of coaxial cable provided by American Signal Corporation.  Make all necessary connections: AC power, coaxial cable to RTU-ISI, antenna to coaxial cable, audio output to fire panel.

The EH&S Fire Safety Systems section will test and commission the Indoor Siren Interface commensurate with manufacturer’s requirements prior to substantial project completion.

VOICE-OVER-IP (VoIP) TELEPHONY:

All structures equipped with new Voice-Over-IP (VoIP) telephony technology should include capabilities for mass notification (public address).  Consult with the Department of Environmental Health & Safety, Emergency Management Section for opportunities to incorporate connections to the FSU ALERT emergency notification and warning system.  For example, desktop telephone handset units should include handsfree speaker capabilities, addressable for mass notification / paging.  Virtual telephony through computers should also include mass notification / paging capabilities. IP-based paging systems or speakers can be easily integrated into FSU ALERT.

DIGITAL DISPLAYS (including televisions):

All structures equipped with new forms of digital displays (televisions, LED signage, electronic displays, kiosks, LCD projectors), indoor or outdoor, should include capabilities to connect to the FSU ALERT emergency notification and warning system.  Consult with the Department of Environmental Health & Safety, Emergency Management Section, prior to design and installation of such displays,  Most modern electronic display systems are IP-addressable and easily integrated with the FSU ALERT system technology.

END OF SECTION

99

SECTION 16000 - ELECTRICAL

Part 1 - General:

1.1	Scope of  Section

This  section  contains  the  requirements  relating  provision  of  electrical  service,  including  utility infrastructure, distribution methods, materials and equipment, electrical energy management, emergency power requirements, circuit coordination, transformers, lightning protection systems, and lighting. Protection of existing electrical equipment, utilities procurement, utility disconnects and locates are included in Division 1- General Requirements.

1.2	Overview

A. 	Connection to Existing Utilities: 	All utility work shall be coordinated with and

approved by the Utilities Section through the construction Project Manager. Each 
drawing that shows a connection to existing utilities shall have a note stating the 
Contractor shall request permission for all outages a minimum of (14) days in advance, 
unless an emergency arises. Explicit details shall be shown for all connections to existing 
utilities. The Utilities Section must approve both the location and the method of the 
proposed connection.

B. 	Electric Consumption During Construction:  The Contractor, through

the Project Manager, shall pay for all electric energy consumed during

construction as part of the project General Conditions. The Contractor

shall obtain the Utilities Procurement Procedures from the Project

Manager.  Requirements for establishing service are as detailed.  Drawings shall clearly call for the Contractor to take such action.

C.	General Material Requirements:

1.  All electrical materials and equipment shall be UL or ETL listed. CSA 
	is not considered equivalent.

2.  All materials and types of construction shall meet or exceed the  requirements of UL, 
	ANSI, NEMA, IEEE, and the NEC as well as conform to manufacturer‘s written 
	recommendations.

D. 	As-Built Drawing Requirement:   Record Drawings that accurately reflect the actual

installed conditions shall be furnished at the end of the project.  Consult with the Project Manager for details of this requirement.

100

E.	Geo-Referencing:  All site plan drawings shall be geo-referenced to the NAD 1983 State

Plane, Florida North 0903, US Foot.  This would include, but not be limited to, showing utilities (existing and new), area lights, blue lights, building foot print, sidewalks, roadway/street edges, parking lots, other impervious data, etc.

F. 	Systems Observation/Training:   An authorized representative(s) of the Owner shall

witness an operational demonstration of completed systems. Representative(s) shall be completely  instructed  in  the  operation  and  maintenance  of  installed  equipment. Representative(s) shall sign and date a statement that confirms they‘ve received proper, comprehensive training.

Part 2 - Materials:

2.1     Conduits

A. 	Exterior lighting:    Schedule 40 PVC is permitted for exterior lighting,

minimum 1‖, and buried to a depth called for by the NEC. When a Quazite junction box is installed near a pole location, a ¾‖ conduit may be used from the junction box to the pole.  If no junction box is installed, the 1‖ conduit shall extend to the pole foundation.

1.	PVC bends shall be made with a hot box.

2.	Factory made bends are acceptable.

3.	Use of flames or hairdryers to fabric bends is unacceptable.

B.	Buried metallic conduit:       PVC shall be converted to metallic where

exposed to physical damage. Buried metallic conduit must have,

minimum, two coats of bitumastic or have factory applied PVC coating.

D.	Empty Conduit:  All empty conduits shall have a 200-pound test pull

cord.

E. 	Conduit shall be manufactured in the United States.

101

2.2	WIRES AND CABLES

A.	Conductors:  All conductors shall be copper with insulation Type

THHN/THWN.

B.	Minimum power conductor size:	#12AWG.

C.	Control conductor sizes and color-coding shall be as governed by

approved wiring diagrams or schematics.

1.	Sizing: Power conductors shall be sized for maximum 5% voltage

drop from source to point of utilization.

2.	Wire type:  In general, conductors #10 and smaller shall be solid,

unless the application specifies stranded wire.  Conductors larger than

#10 shall be stranded.

2.3 	Wire and Cable Connections to Main Electric Service Equipment

A. 	Wire and cable connected to main electric service equipment, utilizing factory or field

installed bus bar, sizes 4/0 and larger shall employ copper to copper 2- hole, compression 
lugs (long barrel only) using ½‖ bolts, 2 flat washers, and 1 split lock washer.  All bolts 
and hardware shall be stainless steel or bronze (equal to Burndy Durium style}. Copper 
Clad connectors will be acceptable.  All Aluminum connectors shall not be used.

B.	Connections made to breakers that are furnished with factory installed mechanical

connectors  will  be  allowed.	For  mechanical  connectors,  factory  recommended

installation procedures shall be employed (connector torque settings, the use of oxide

inhibiting compound, etc).

2.4	MC Cable

A. 	All wire and cable shall be installed in conduit or where applicable, tray-rated cable in

cable trays.    In lieu of wire in conduit, MC cable may be used in areas allowed by the NEC, but only with the joint approval of the Engineer of Record, the FSU BCA, FSU Utilities Department, and FSU Plan Reviewers

B.	In new and remodeling construction, MC cable shall not be used inside new walls.

102

2.5	Conduit Systems Identification

A.	Conduit systems shall be identified by the color code listed below.   If a color code is

already in use in a building, then that code will be utilized for that building.  If no code is

in use, then this one shall be used.  If an existing building system is being modified, these

requirements apply only to the new raceway systems.

SYSTEM	COLOR

Fire Alarm	Red

mergency Power (Life Safety Branch)	Yellow

Critical Branch	Orange

Equipment Branch	Green

Essential Distribution	Purple

(Genset Output to Line Side of ATS)

Normal Power	Blue

Security	Brown

B.	The last six inches of conduits, their junction boxes, and their covers shall be painted the

appropriate color.

C.	For power conduits, the circuits involved shall be identified on the junction box covers

using a black permanent marker.

D.	For unique colors associated with telephone or data cable raceways, see appropriate

paragraphs of OTC requirements.

2.6	PANELBOARDS

A.	Identification:   Panelboards shall be identified using permanently attached machine

engraved phenolic nameplates.

1.  Standard color shall be white letters on black background. 
	103

2.  Emergency panels shall have white letters on a red background.

B.	Panelboard bus shall be copper.

C.	Rating:  Lighting and receptacle panelboard neutral bus shall be rated 100%.

D.	Sizing:  Panelboards shall be sized for minimum 25% spare above calculated diversified

demand loads.

E.	Breakers:   Circuit breakers shall be bolt-on construction. Devices shall be rated for the

calculated available bolted fault short circuit currents.

1.  Copies of the fault current calculations shall be furnished with plans 
	prior to construction to the Project Manager for review.

2.  If breakers are to be used for switching, switching duty breakers shall 
	be used.

F. 	Main Distribution panels shall have metal oxide varistor (MOV) type surge protection

device (SPD).   The MOV device shall have a short circuit current rating of 200 kA or greater.  The MOV shall be rated for service voltage of the facility.

1.  MOV(s) shall be installed in the first ‗down line‘ panel and

other locations deemed necessary by the Engineer of Record.  This type MOV shall be sized as appropriate for the installation as determined by the Engineer of Record.

2.  Acceptable manufacturers are:  Square D, Siemens, and General 
	Electric.

2.7	Switches and Receptacles

A.	Switches and receptacles shall be specification grade and rated 20

amperes.

B. 	Color:  Standard shall be ivory with stainless steel plates.  Different color devices must

be approved by the Engineer of Record and the Project Manager.

104

C.	Emergency receptacles:  Devices assigned to the emergency system shall be distinctive

in color: red is considered standard unless another color

D.	Receptacle spacing:

a.    Vending areas shall have outlets mounted no greater 
	than 48‖ on center.

2.  Hallways shall have outlets mounted 50 feet on center, maximum.

E.  Receptacle mounting height:  Device mounting heights shall conform to the latest 
	applicable edition of ADA standards.

a.  Floor outlets shall be flush with finished floor or floor covering, as applicable.

b.  When required for classrooms, receptacles for overhead LCD projector 
	shall be mounted flush with ceiling.

E.	Vending/Wet Locations:  Outlets serving vending machines shall be GFI receptacles on

separate circuits.

F.	Building Exterior:   Outlets shall be provided on the exterior of facilities located

according to the geometry of the footprint of the facility and good design, so that their

spacing does not exceed 100 feet on center.

2.8 	MOTORS, DISCONNECT SWITCHES AND STARTERS

A. 	Motors: Shall be high efficiency and have an operating power factor of

90% or greater. Provide reduced voltage starters or variable speed drives

for all motors 15 horsepower, or larger.

1.  Variable speed drives shall be connected to the campus-wide energy management 
	system.  For detailed requirements for these connections, contact the FSU Utilities 
	Section.

2.  Acceptable Manufacturers of VFDs and Soft Starts are:

a.  VFDs: AC Technologies; Yaskawa; ABB; Danfoss (under 125 
HP);

b.  Soft Starts:  SAF

3.  Acceptable manufacturers of disconnect switches are:  Square D, 
	Siemens, and General Electric.

105

2.9	POWER GENERATION

A. 	Emergency Power Source:  Where required for life safety per NFPA-101

and/or for continuity of function in certain facilities, provide a standby rated emergency 
power engine generator set. The addition of  battery-powered lighting, instead of 
providing  a  generator  set,  to  meet  NFPA-101  exit/egress  requirements  is  highly 
discouraged.

B. 	Engine Generator Set: Shall be diesel fueled unless so small that diesel prime mover is

not commercially available. Natural gas and LP fueled sets are unacceptable. Fuel tank

shall be sized for minimum 36 hours of operation at full load.  ‗Full tank‘ shall be defined as 7/8 tank capacity and shall provide 36 hours of operation at full load.  Larger tanks may be required to serve facilities where continuity of function is mandatory. The 
operation and fueling requirements for those types of facilities shall be handled on a 
project-by-project basis as design criteria through the Project Manager.

1.  Acceptable Manufacturers:  Engine generator sets shall be

Caterpillar,Cummins/Onan or Tradewinds.  All other manufacturers are unacceptable.

C.	Generator Set Location:

1.  There are numerous locations on campus where terrain or geometry of adjacent

structures may require that the generator set be installed in a sound attenuating

enclosure with a rated sound attenuating silencer. This requirement will need to be discussed during initial design meetings and the actual level of attenuation 
determined early in the design process.

2.  Generator sets shall be installed on building exteriors except possibly for locations 
	such as energy/utility plants.

3.  The location of the generator set shall be coordinated with the relative location of the 
	fresh air intake for the building to minimize the intrusion of the generator‘s exhaust 
	fumes into the building fresh air intake system.

4.  Unit shall be located and physically protected in such a manner as to reduce the 
	vulnerability to damage by vehicles, severe storms or hurricanes.

D: 	Fuel tank location/Platform:  Shall be above ground and approved by EPA. If fuel tank

is of such dimension that the top of the mounting skid is 24‖ or greater AFG, then a substantial maintenance platform shall be constructed around all sides.  Platform shall be in full accordance with all applicable OSHA safety standards for handrails, etc.

E.	Generator Start:  Generator set shall be started electrically using its own properly rated

and sized batteries. Air start is unacceptable.

106

F.	Connection to Building Power Distribution:   Engine generator set shall connect to

building power distribution system through coil and contactor operated automatic transfer switche(s) (ATS). ―Walking Beam‖ switches are unacceptable. Transfer switch shall have an integral, field adjustable automatic exerciser clock.

G. 	If a four pole ATS is employed, the neutral switching operation shall be a ‗make before

break‘ on transfer to emergency power and re-transfer to normal power.

H.          Minimum Emergency Services:  In addition to other requirements, the

generator set shall have the capacity to serve, as a minimum, one elevator, 
building access control panels, all building data gathering panels used for 
HVAC control and management systems, steam condensate return pumps, 
and sump pumps.

I. 	Generator Sizing:  Shall be for minimum 25% spare above calculated

diversified demand loads. Greater than 25% spare capacity may be 
required.  Consult with FSU Project Manager for percentage spare 
capacity.

J. 	Reference Standard:  Generator shall conform to ISO-9001; have Class H

insulation, and permanent magnet excitation for production of 300% of

rated full load current for ten seconds.

K.        Acceptance Testing:  Generator set on-site acceptance testing shall be

performed in accordance with NFPA-110 at 80% and 100% power factors.

1.  The acceptance test shall be a minimum of 4 hours at 80% PF utilizing a 
	resistor/reactive load bank device.

2.  Generator Shop personnel shall be notified of the test schedule min.

(72)hours in advance so that they may attend.

3.  The contractor shall furnish a full tank of fuel at the completion of all 
	testing.  Full tank shall be defined as 7/8 tank capacity.

L. 	Generator Cooling:  Generator set shall be cooled with self-contained

coolant and radiator system.  Remote coolers are unacceptable.

107

M.          Maintenance Manuals:  Equipment supplier shall supply two operation

and maintenance manuals. Deliver one to the Project Manager and one directly to the Generator Shop Supervisor.

N.	Warranty:  All systems shall have a five-year warranty, unless the project

considerations dictate differently and is approved by FSU Maintenance

Department.

2.10	SERVICE AND DISTRIBUTION

ELECTRIC SERVICE:

Electric service to buildings and facilities on campus will normally be served from FSU‘s 15 KV (12,470V) medium voltage distribution system.  If a building is not served from an existing sectionalizing device, a new SF6 gas insulated vacuum fault interrupter device shall be installed.  Interrupters shall have 600-ampere separable quick change bushings.   G & W is the only acceptable manufacturer.   A 35 lb bottle of SF6 gas shall be supplied with all new sectionalizing switch installations.

Service to buildings shall be supplied from pad-mounted transformers as described below.    The transformers, service entrance conductors or bus, and main electrical panel or equipment shall be of adequate size for the demand expected in the facility and to allow for future growth of 25% based on calculated diversified demand.

Transformers shall be located as close as possible to the main electric service room.  Future servicing or replacement of transformers shall be a consideration when selecting a location.  The transformer shall be protected from vehicular and pedestrian traffic.

Refer to the Wire and Cable Connections to Main Electric Service Equipment for allowable types of connections.

The location of the building electric service apparatus shall be incorporated in the landscaping as much as 
possible.

108

METERING

A watt-hour meter with a demand register shall be provided for each building. This shall be coordinated through the University Project Manager with the Utilities Section.

For buildings being served by a pad mounted transformer, the meter location shall be on the transformer. Metering current transformers shall be installed in the secondary compartment of the transformer.  A 1‖ conduit shall be installed from the pad to the nearest building system control junction box. If metering equipment is installed in the main switchgear of a building, a separate meter compartment in the switchgear shall be utilized

GROUNDING

All grounding for building services, standby generators, and transformers shall achieve a maximum 10-
ohms or less as required by specific project criteria, using the three-point test method.   If necessary, 
multiple rods shall be driven to achieve the desired resistance to ground.  All grounds shall be connected 
with a properly sized copper conductor.  All ground busses shall be connected to ground rods by either (1) 
an approved exothermic welding process as manufactured by Erico or (2) a compression system as 
manufactured by Burndy known as ‗Hyground‘.     Each rod shall be tested in the presence of the 
University's representative.   A written record of the test results shall be prepared and signed by the 
contractor and University‘s representative.  This record shall be submitted to the Architect/Engineer and 
supplied to the University with the ―Record Drawings‖ and reports upon the completion of the project.

Circuit Coordination

It is the responsibility of the Architect/Engineer to insure the proper electric circuit coordination. 
	15KV Distribution System

All new circuit and transformer installations shall be properly coordinated with the existing electric distribution on campus.   The Engineer shall furnish circuit coordination parameters including relay/fuse settings, time-current characteristic curve plots, and verification that all settings have been made.

Existing substation breaker settings and available fault current data (at FSU‘s substation) will be made available, upon request, from FSU‘s Utility Department.   The Engineer must produce coordinated time current curve characteristic plots of his proposed settings for review and approval by FSU Utilities Section prior to energizing.

Facility Electrical Systems

The Engineer shall provide breaker settings for all new or remodeled building electrical systems. Circuit coordination parameters shall be furnished, including time-current characteristic curve plots, breaker/relay settings, and verification that all settings have been made.

109

New Construction:   Adjustable breakers installed down line of the main switchgear shall be coordinated with the main breaker.   Calculations, time current curves and settings shall be furnished with the record drawings.  The Engineer of Record shall be responsible for setting of all adjustable breakers.

Remodeling:

For projects that are remodeling in nature and do not encompass the whole electric system, only the electric equipment involved in the remodeling will require circuit coordination settings.

Arc Flash Data

The Engineer shall provide arc-flash data for all electrical systems installation as required by the NEC, NFPA-70E, and all local codes.

Pertinent signs pertaining to arc-flash information shall be prominently displayed on all equipment involved, i.e. Panelboards, switchgear, motor controllers.

Pad-Mounted Transformers:

In order to provide better circuit coordination in the University’s electrical system, a service transformer’s base rating shall not exceed 2000KVA.     If additional capacity is required the design professional must consider either multiple transformers or specifying units that are dual temperature rated and equipped with forced air-cooling.

The phase overcurrent device simulated in the SF6 switch must be compatible with the campus system‘s feeder breakers in order to achieve proper circuit coordination.  If requested, a copy of the feeder breaker time-current characteristic curves will be furnished by FSU for use by the design professional prior to the time required for the incoming service to be energized

Basic description, features, accessories:

Insulating fluid - Envirotemp FR3

Winding Material - Copper or Aluminum

Primary Voltage, 12470 delta - 95 KV BIL

Taps - 2 @ 21/2 % above and 2 @ 2 ½ % below normal Configuration - Dead front, radial feed

Primary Bushings - Three Wells, 15 KV, 200-amp Inserts - Feed through

Secondary Bushings - Spade Terminals

Fusing - Bay-O-Net oil immersed in series with ELS-P Impedance - NEMA Standard with standard tolerances Color - Bell Green

Standard Features:

o  MOV arrestors

110

o  Provisions for bushing mounted CT‘s

o  Stainless steel grounding pads in HV and LV compartments o  Removable neutral ground strap

Standard Accessories:

o	1‖ fill plug

o	1‖ drain valve and sampling device in HV compartment

o  Dial type thermometer 
o  Liquid level gauge 
o  Pressure vacuum gauge 
o  Pressure relief valve.

All conductor connections to padmounted transformers shall be installed using 2-hole compression lugs, ½‖ bolts, 2 flat washers and 1 lock washer for wire size 4/0 and larger.  All connection hardware shall be bronze equal to Burndy Durium type.

Acceptable manufacturers are: Cooper - Waukesha, Wisconsin; Howard - Laurel, Mississippi; or General Electric - Shreveport, Louisiana.

111

MEDIUM VOLTAGE CABLE

Medium voltage cable shall be copper, 105 degrees C rated, EPR with 133% insulation.  Cable size shall be 350 KCMIL for feeders.   Transformer feed cable shall be 2/0, 1/0 or #2 (minimum).   Cable shall be manufactured by The Okonite Company or The Kerite Company.

All new 15KV cable shall be proof tested according to manufacturer‘s recommendations prior to being energized.

DUCT BANK SYSTEMS

All 15 KV cable shall be installed in duct bank system as follows:

1.  All ducts shall be encased in at least 3‖ concrete on all sides, top and bottom.

2.  Ducts may be EB-20, EB-35, or schedule 40 PVC conduit.  Conduit shall be parallel and 
	separated by appropriate spacers.  Conduit shall be sized as required for the project.

3.  Duct banks shall have sufficient number of conduit for the project plus a minimum of two spares. 
	Conduits from 15 KV switches to transformers will require only one spare.  If future use may 
	require additional circuit installation, then more spare ways may need to be installed.

4.  Duct banks shall be a minimum depth of 36‖ to the top of concrete.  Where duct banks are less 
	that 36‖ or in locations that require protection, a layer of ‗flowable fill‘ with red dye shall be 
	installed over the duct bank.  The flowable fill layer shall come to within one foot of finished 
	grade or, if under a paved area, to the bottom of the asphalt base or concrete pavement.

5.  A 4/0 copper ground loop conductor shall be installed with all duct banks, regardless of number 
	of ways.  The ground loop conductor shall be located in the center of the top of the concrete 
	encasement

6.  All duct bank installations shall be inspected by the Engineer of Record, FSU‘s BCA, and FSU‘s 
	Utility Department Representative prior to encasing in concrete.

7.  If a duct bank is within 8‘ laterally or crosses a steam line, coordinate with FSU‘s Utility

Department to insure sufficient additional heat barrier insulation is installed to prevent damage to the duct bank and electric cables.

MANHOLES

Manholes shall have the following basic physical description:

Inside dimensions of 8‘-0‖ octagonal made from minimum 2500 PSI concrete. Duct entrances supplied with end bells

Minimum clearance from centerline of lowest duct entrance shall be 2‘-0‖to floor Minimum 8‖ thick walls, minimum 6‖ thick floor for sump

Duct face at corners a minimum of 18‖ wide

112

Cable racks shall be heavy duty, galvanized, with porcelain cable saddles. Pulling irons fabricated from 
hot-dipped galvanized steel bars shall be provided in walls opposite duct entrances. Cables shall loop 
manhole prior to exiting on through-pulls and shall pass by two adjacent complete faces, as a minimum, 
on angle pulls.

Covers shall conform to Specification RR-F-621 with vent holes and, minimum, two pick holes. Pick 
holes shall be minimum ¾‖ diameter. Cover shall be approximately 32-½‖ diameter and manufactured by

U.S. Foundry, or equal.

Each manhole shall contain a 4/0 ground loop, mounted 18‖ above the floor, bonded to a ground rod that 
measures 10 ohms to ground or less. Ground loop shall bond all non-current carrying conductors in each 
manhole and shall be bonded to the ground loop conductor routed with the duct bank systems.  Bond shall 
be by exothermic means or compression using a Burndy ―Hyground‖ system. No other compression 
system is acceptable.

LIGHTNING PROTECTION SYSTEMS

All buildings/structures shall have appropriate lightning protection systems designed and installed in 
accordance with NFPA-780. Installer shall be LPI certified. Installed system shall bear a Master Label.

Expansions of existing facilities shall upgrade the existing lightning protection system as required to obtain or maintain a Master Label for the envelope.

LIGHTING SYSTEMS

General:

All lighting designs should comply with the current edition of the Illuminating Engineers Society (IES) standard, except where specifically directed for different foot candle levels.

Interior Lighting:

The standard lighting system shall utilize fluorescent T8 or T5 lamps with electronic ballasts having a 
total harmonic distortion (THD) of less than 10%.   Interior systems that are not dimmed shall employ 
28W lamps where ambient temperatures and other conditions are suitable for their application.

113

Dimmable systems shall use 32W lamps.    Wherever possible, four-foot lamps are to be used.  T5 lamps may be used when required by project design.

Light fixtures in stairways shall be above the landings and not above the steps.

Automatic light controls shall comply with Chapter 13, Energy Efficiency, of the Florida Building Code.

Emergency lighting shall be provided at all exits and in all stairways, hallways, mechanical rooms and elevators according to NFPA-101. Emergency lighting shall be powered from the building emergency generator system. Battery powered emergency lighting shall not be used unless there is no emergency generator associated with the project.

Where emergency lights are required in classrooms, a bypass switch shall be installed to permit the light to be switched off during special presentations.   During actual power failures, the bypass shall be rendered inoperative.

No lights shall be installed that require scaffolding for relamping.

Exit lights shall be of the Light Emitting Diode (LED) type.

Building Lighting Level requirements

The following recommended lighting levels shall be used as a general guide:

1.  Hallways, Restrooms	20 Foot Candles (FC)

2.  Classrooms	50 FC

3.  Offices	40 FC

4.  Laboratories	As required

5.  Mechanical/Electrical Rooms	30 FC

6.  All other areas	As required.

Approval from FSU‘s Utility Department and Project Manager is required for variations from the above foot candle levels.

114

Classroom Lighting:

Classroom lighting shall comply with DOE requirements.  Lighting in classrooms and lecture halls with seating capacity greater than 25 people shall be equipped fluorescent dimming systems.

Approved dimming system manufacturers are:

1.  Lutron ‗Hi-lume‘ system

2.  Lutron Eco-10 system with Hi-lume 3D ballast where 1% dimming is required.

3.  Universal Lighting Technologies DaliPro system

4.  Creston

All dimming system shall employ switching scenes that will return emergency lights to full brightness upon loss of normal electric power.

For detail requirements for dimming and occupancy sensor systems refer to Appendix E, Design Criteria and Requirements for Classrooms at Florida State University.

BLUE LIGHT SYSTEM

The AE shall include new locations for the University‘s system of emergency blue lights, as appropriate for the project.

The FSU Department of Public Safety shall determine the location of blue lights.

The FSU Department of Environmental Health & Safety, Emergency Management Section shall review emergency blue light placement and potential need to upgrade units with voice loudspeaker capability.

For additional information see Florida State University, Telecommunications Infrastructure Standard -
FSU Design Guidelines Appendix ‗A‘.

OUTDOOR LIGHTING

Outdoor lighting on the FSU campus shall be attractive and in keeping with the standards set forth in this section. The lighting plan shall be energy efficient while maintaining appropriate light level(s) as prescribed in the latest edition of the NFPA codes and IES handbook for high activity facilities.

When outdoor lighting is associated with a building project, security lighting and parking lot lighting shall be included in the building design.

No lights are to be installed that require scaffolding for relamping. Pole mounted parking lot and walkway lights shall be bucket truck accessible.

Walkway and exterior security lighting shall be controlled by a photoelectric cell and contactor, with a manual override for maintenance.

Security of all areas shall be carefully considered when locating outside lights on buildings or on poles.

115

Outdoor lighting shall be period style fixtures, pole mounted where possible. Poles and fixtures shall be: 
	Fixtures:

All fixtures shall use high-pressure sodium lamps. All ballasts shall be multi-voltage tapped (120,208,240, and 277-volt taps).   Globes/diffusers shall be glass.   Plastic is unacceptable.   Precision injection-molded, UV stabilized; acrylic lens is acceptable for parking deck fixtures.

Walkway and roadway type fixtures:

Fixture trim shall be black.  Acceptable manufacturers are:

A.   Holophane - Utility Series Granville with black finial or

B.  Sternberg Hometown Series with acorn glass globe.

Parking Lot Fixtures:

Fixtures shall be black.  Acceptable manufacturers are:

A.  Gardco - Gullwing Series (G18 series).

B.  Lithonia Lighting - Aeris AS2 Series with decorative curved arm.

Parking Deck Fixtures:

Acceptable manufacturers are:

A.  Lithonia - PGR Series with 100-watt HPS lamps.  Fixtures shall be dark bronze with 
	offset junction box mounting feature.  (QRS is a quartz restrike option where such is 
	desired).

B.  Gardco - Quadra Series fixture with 100-watt HPS lamps.  Fixtures shall be dark bronze 
	with offset junction box mounting feature.  (QRS is a quartz restrike option where such is 
	desired).

Poles shall be 12‘ Holophane Mount Vernon series or Sternberg Somerset (2700-FP) series 
fluted aluminum for streets and walkways.   Parking lot poles shall be square aluminum of 
appropriate height.    All street and walkway poles shall be black.  Parking lot poles shall be 
bronze.  Poles shall be mounted on poured concrete bases.  Bases shall be installed at grade 
level on asphalt, concrete or brick paving; at 6" A.F.G. along walkways and streets; at 30"

A.F.G. in parking lots.

Light fixtures and poles shall be separate items (no combination units).

PARKING DECK LIGHTING

The consultant shall evaluate the feasibility of installing lighting control systems that monitor and control the ―interior‖ and ―exterior‖ zones lighting according to available ambient levels.   The control systems shall be field adjustable to owner‘s specifications.

A control system recommendation shall be presented to the Project Manager no later than the 50% plans submittal.

END OF SECTION

116

THIS PAGE INTENTIONALLY LEFT BLANK

117